## IRK calculation
DESCRIPTION
Before Expansion
Baseline
In May 2006, PT. Indo Raya Kimia (IRK) expands its production capacity to 145-150 t/d by upgrading SRU blower (K-504) from 315 kW to 400 kW. Due to production increase, 11.95 t/h of steam is generated from the SRU and furnace. After internal consumption, 10.10 t/h of waste steam is released to the atmosphere. Total power requirement of IRK is met from PLN Jamali grid.
Project
In the project activity, the amount of 10.10 t/h of 24 barg steam from the SRU and furnace which was un uitilized is proposed to generate electricity. This will be done by using this waste heat to run 1.2 MW installed steam turbine generator. This new set-up, will help to generate 1.2 MW power thereby catering total power requirement of IRK plant. Electricity import from the grid would only be required in case of emergency, stoppage of turbine and annual shut down for maintenance. As a result, IRK will reduce the electricity from PLN about 7,603 MWh in a year.
Utilization of new turbine in CS2 plant - Sept 2008
DESCRIPTION |  | SYMBOL | AMOUNT |  | UNIT | REMARK | SOURCE
| Operating hours |  | = | 24 | h/d |  | IRK
|  |  | = | 330 | d/y |  | Bill of Material report & YTD production summary
Baseline
| Capping factor | fcap | = | 1 |  |  | As per section ACM0012 ver 03.2
| Fraction of total electricity generated by the project activity using waste energy | fWCM | = | 1 |  |  | According to AMS III.Q ver 04, this fraction is 1 if the electricicty generation is purely from use of waste energy
Production capacity | Production associated with the relevant waste energy generation as it occurs in the baseline scenario. | QBL, product | = | 147.8676 | t/d |  | Historical data of CS2 plant operation for the 6 months (May -June '06, Jan - April 07) during the operational of electric blower of 400 kW in normal condition, which the steam produced was un utilized and emitted to the Atmosphere.
Electricity | The quantity of electricity supplied to the recepient j by generator, that in the absence of the project activity would have been source from grid during the year y | EG i,j,y | = | 7603.2 | MWh/y |  | Considering 0.8 of load factor, total power it can generate (1.2 MW * 24 h/d * 330 d/y = 7,603.20 MWh/y) is less than the electricity consumption for the CS2 production. Then this figure is taken as quantity of electricity supplied to the recepient j by generator, that in the absence of the project activity would have been source from grid during the year y
Emission factor | Emission coefficient of PLN Jamali grid | EFElect,i,j,y | = | 0.862 | tCO2 e/MWh |  | Emission factor from PLN Jamali grid refer to Tool to calculate the emission factor for an electricity system v02
Baseline emission | Baseline CO2 emissions from total electricity consumption during the year y | BEy | = | 6553.9584 | tCO2 e/y |  | Calculation
Project
Electricity | Internal power consumption | EC internal, y | = | 146 | kW |  | Internal power plant : a. condensate extraction pump I (CEP I) = 11 kW b. cooling water pump A (P-906/P-907) = 90 kW c. cooling tower fan (P-908) = 45 kW
|  |  | = | 1156.32 | MWh/y
| Electricity consumption from grid by the project activity during start up |  | = | 0 | MWh/y |  | in the PDD development, the amount of electricity consumed from PLN grid by the project activity during start up is considered zero but it will be measured and monitored during the crediting period.
Project emission |  | PEy | = | 996.7478 | tCO2 e/y
Emission Reduction |  | ERy | = | 5557.2106 | tCO2 e/y |  | Calculation
Emission Reduction
|  |  |  | Year | Estimation of Baseline Emission (tCO2 e/y) | Estimation of Project Emission (tCO2 e/y) | Emission Reduction (tCO2 e/y)
The starting date of the crediting period is 01/10/2012 |  |  |  | 2013 | 5461.632 | 830.6232 | 4631.0088
|  |  |  | 2014 | 6553.9584 | 996.7478 | 5557.2106
|  |  |  | 2015 | 6553.9584 | 996.7478 | 5557.2106
|  |  |  | 2016 | 6553.9584 | 996.7478 | 5557.2106
|  |  |  | 2017 | 6553.9584 | 996.7478 | 5557.2106
|  |  |  | 2018 | 6553.9584 | 996.7478 | 5557.2106
|  |  |  | 2019 | 6553.9584 | 996.7478 | 5557.2106
|  |  |  | 2020 | 6553.9584 | 996.7478 | 5557.2106
|  |  |  | 2021 | 6553.9584 | 996.7478 | 5557.2106
|  |  |  | 2022 | 6553.9584 | 996.7478 | 5557.2106
|  |  |  | 2023 | 1092.3264 | 166.1246 | 926.2018
|  |  |  | Total | 65539.584 | 9967.4784 | 55572.1056
|  |  |  | Average | 6553.9584 | 996.7478 | 5557.2106

## Resume
CDM PROJECT
PT INDO RAYA KIMIA
Month | CS2 Production |  | Steam Generation |  |  | Use for
|  |  | from Claus Unit/SRU, by FI-5091 | From CS2 Plant/Furnace, by FI-2007 | Total Steam generated | CS2 Sep. and WWS | K-503 | Excess, condensed in Fan Condenser
| TPM | TPD.Average | TPH | TPH | TPH | TPH | TPH | TPH
Source | Bill of Material report & YTD Production summary |  | TPSDDE through DCS |  | Calculation | Basic Engineering Package from Akzo nobel | TPSDDE through DCS | Calculation
2004-01-01 | 2633.35 | 121.35 | 9.4648 | 0.26411 | 9.7289 | 1.5169 | 7.5844 | 0.62769
2004-02-01 | 3831.16 | 133.84 | 11.9795 | 0.54482 | 12.5243 | 1.673 | 8.365 | 2.4863
2004-03-01 | 4197.38 | 135.4 | 12.3986 | 0.54684 | 12.9455 | 1.6925 | 8.4625 | 2.7905
2004-04-01 | 3878.95 | 129.2983 | 12.099 | 0.48682 | 12.5858 | 1.6162 | 8.0811 | 2.8884
2004-05-01 | 1812.68 | 118.0899 | 11.1264 | 0.63477 | 11.7612 | 1.4761 | 7.3806 | 2.9044
2004-06-01 | 4046.61 | 136.8022 | 12.5975 | 0.94879 | 13.5463 | 1.71 | 8.5501 | 3.2861
2004-07-01 | 3922.31 | 126.5261 | 12.0224 | 0.91478 | 12.9372 | 1.5816 | 7.9079 | 3.4477
2004-08-01 | 3402 | 127.4157 | 11.6137 | 0.93799 | 12.5517 | 1.5927 | 7.9635 | 2.9956
2004-09-01 | 2257.72 | 119.7094 | 11.709 | 0.90736 | 12.6163 | 1.4964 | 7.4818 | 3.6381
2004-10-01 | 3038.24 | 115.9634 | 10.1824 | 0.87329 | 11.0557 | 1.4495 | 7.2477 | 2.3584
2004-11-01 | 3766.72 | 131.9804 | 9.6835 | 0.99424 | 10.6778 | 1.6498 | 8.2488 | 0.77924
2004-12-01 | 4004.32 | 131.3753 | 9.7347 | 1.0563 | 10.791 | 1.6422 | 8.211 | 0.93785
2005-01-01 | 2504.99 | 132.42 | 9.5977 | 0.59931 | 10.197 | 1.6553 | 8.2763 | 0.26551
2005-02-01 | 3570.71 | 136.1308 | 8.9632 | 1.0599 | 10.0231 | 1.7016 | 8.5082 | -0.1867
2005-03-01 | 3878.1 | 129.7023 | 9.204 | 1.1149 | 10.319 | 1.6213 | 8.1064 | 0.59131
2005-04-01 | 2071.98 | 124.4432 | 9.1543 | 0.98203 | 10.1363 | 1.5555 | 7.7777 | 0.80307
2005-05-01 | 3838.25 | 126.1027 | 9.5182 | 0.99397 | 10.5121 | 1.5763 | 7.8814 | 1.0544
2005-06-01 | 3679.63 | 122.6543 | 9.1276 | 1.0139 | 10.1414 | 1.5332 | 7.6659 | 0.94237
2005-07-01 | 3838.85 | 123.83 | 9.6735 | 0.90197 | 10.5755 | 1.5479 | 7.7394 | 1.2883
2005-08-01 | 3060.31 | 115.31 | 9.7195 | 0.99597 | 10.7154 | 1.4414 | 7.2069 | 2.0672
2005-09-01 | 1584.26 | 136.1 | 9.6091 | 0.97084 | 10.5799 | 1.7012 | 8.5062 | 0.37245
2005-10-01 | 4083.82 | 135.7 | 9.6714 | 0.89959 | 10.571 | 1.6962 | 8.4812 | 0.39347
2005-11-01 | 3068.13 | 22.52 | 9.2239 | 0.86431 | 10.0882 | 0.2815 | 1.4075 | 8.3992
2005-12-01 | 3329.65 | 136.07 | 9.2239 | 1.0255 | 10.2494 | 1.7009 | 8.5044 | 0.044179
2006-01-01 | 4074.627 | 138.3457 | 10.1426 | 0.98266 | 11.1252 | 1.7293 | 8.0058 | 1.3901
2006-02-01 | 3945.63 | 140.9154 | 10.3155 | 1.1091 | 11.4246 | 1.7614 | 8.8072 | 0.85591
2006-03-01 | 4311.27 | 139.0732 | 10.0949 | 1.0589 | 11.1538 | 1.7384 | 8.6921 | 0.72334
2006-04-01 | 1894.017 | 129.9051 | 10.2891 | 0.7485 | 11.0376 | 1.6238 | 7.1719 | 2.2418
Project Start Up
Month | CS2 Production |  | Steam Generation |  |  | Use for
|  |  | from Claus Unit/SRU, by FI-5091 | From CS2 Plant/Furnace, by FI-2007 | Total Steam generated | CS2 Sep. and WWS | Steam to Condensing Turbine | Excess, condensed in Fan Condenser
| TPM | TPD.Average | TPH | TPH | TPH | TPH | TPH | TPH
Source | Bill of Material report & YTD Production summary |  | TPSDDE through DCS |  | Calculation | Basic Engineering Package from Akzo nobel | TPSDDE through DCS | Calculation
2006-05-01 | 3197.22 | 148.572 | 10.7139 | 0.91865 | 11.6325 | 1.8571 | 9.7754 | 0
2006-06-01 | 4456.885 | 149.9337 | 10.9492 | 0.8911 | 11.8403 | 1.8742 | 9.9534 | 0.012698
2006-07-01 | 4549.069 | 146.9417 | 10.7452 | 0.91681 | 11.662 | 1.8368 | 7.8608 | 1.9644
2006-08-01 | 3843.055 | 132.1073 | 9.5224 | 0.7875 | 10.31 | 1.6513 | 8.12 | 0.54
2006-09-01 | 2650.218 | 143.5784 | 10.502 | 0.92749 | 11.4295 | 1.7947 | 8.3729 | 1.2619
2006-10-01 | 4592.568 | 148.3135 | 10.8271 | 0.94298 | 11.7701 | 1.8539 | 9.8531 | 0.063098
2006-11-01 | 4462.3 | 148.9329 | 11.0471 | 0.92173 | 11.9689 | 1.8617 | 8.8278 | 1.2794
2006-12-01 | 4274.94 | 149.063 | 11.1326 | 0.92749 | 12.0601 | 1.8633 | 9.0774 | 1.1194
2007-01-01 | 3632.93 | 140.0018 | 10.2528 | 0.30274 | 10.5556 | 1.75 | 8.8056 | 0
2007-02-01 | 4144.716 | 148.912 | 11.4663 | 0.96353 | 12.4299 | 1.8614 | 10.5685 | 0
2007-03-01 | 4587.833 | 148.2503 | 11.5495 | 1.0129 | 12.5624 | 1.8531 | 10.7093 | 0
2007-04-01 | 4532.186 | 151.5359 | 11.5742 | 1.0828 | 12.657 | 1.8942 | 10.7628 | 0
2007-05-01 | 3983.755 | 147.0925 | 11.3875 | 1.0346 | 12.4221 | 1.8387 | 10.5835 | 0
2007-06-01 | 2996.03 | 142.7153 | 10.9507 | 0.91151 | 11.8622 | 1.7839 | 10.0783 | 0
2007-07-01 | 4475.02 | 144.3555 | 10.9667 | 0.92676 | 11.8935 | 1.8044 | 10.089 | 0
2007-08-01 | 3847.22 | 124.1039 | 9.1234 | 0.79302 | 9.9164 | 1.5513 | 8.3651 | 0
2007-09-01 | 3756.87 | 127.1121 | 9.335 | 0.83981 | 10.1748 | 1.5889 | 8.5859 | 0
2007-10-01 | 4471.39 | 144.2384 | 10.9162 | 1.0072 | 11.9234 | 1.803 | 10.1204 | 0
2007-11-01 | 2516.3 | 125.815 | 10.1488 | 0.8631 | 11.0119 | 1.5727 | 9.4392 | 0
2007-12-01 | 3349.93 | 129.2577 | 10.0099 | 0.83981 | 10.8497 | 1.6157 | 9.2339 | 0
Note on A28: Saktiyo (Asia Carbon Indonesia): CDM Start Date
Note on A41: Saktiyo (Asia Carbon Indonesia): CS2 Expansion
Note on A53: Saktiyo (Asia Carbon Indonesia): COD CDM

## Steam Generation from CS2 Plant
Steam Generation from CS2 Plant, read by FI-2007
Data is taken from TPSDDE (Automatic DCS data) at 08:00 AM
Date | FI-2007 | Date | FI-2007 | Date | FI-2007 | Date | FI-2007 | Date | FI-2007 | Date | FI-2007 | Date | FI-2007 | Date | FI-2007 | Date | FI-2007 | Date | FI-2007 | Date | FI-2007 | Date | FI-2007
| Kg/hr |  | Kg/hr |  | Kg/hr |  | Kg/hr |  | Kg/hr |  | Kg/hr |  | Kg/hr |  | Kg/hr |  | Kg/hr |  | Kg/hr |  | Kg/hr |  | Kg/hr
2004-01-01 | 489.5078 | 2004-02-01 | 310.7477 | 2004-03-01 | 570.0197 | 2004-04-01 | 535.3226 | 2004-05-01 | 329.3854 | 2004-06-01 | 903.1509 | 2004-07-01 | 996.6125 | 2004-08-01 | 912.619 | 2004-09-01 |  | 2004-10-01 |  | 2004-11-01 | 1086.9873 | 2004-12-01 | 1010.698
2004-01-02 | 176.8746 | 2004-02-02 | 420.5859 | 2004-03-02 |  | 2004-04-02 | 499.4735 | 2004-05-02 | 424.2672 | 2004-06-02 | 760.6239 | 2004-07-02 | 960.3226 | 2004-08-02 | 861.258 | 2004-09-02 |  | 2004-10-02 |  | 2004-11-02 | 1317.5675 | 2004-12-02 | 960.8674
2004-01-03 | 163.3735 | 2004-02-03 | 467.9398 | 2004-03-03 | 570.0197 | 2004-04-03 | 641.0927 | 2004-05-03 | 407.1274 | 2004-06-03 | 996.9757 | 2004-07-03 | 701.1826 | 2004-08-03 | 922.5799 | 2004-09-03 |  | 2004-10-03 |  | 2004-11-03 |  | 2004-12-03 | 1027.066
2004-01-04 | 130.0956 | 2004-02-04 | 535.6778 | 2004-03-04 | 529.5655 | 2004-04-04 | 567.4492 | 2004-05-04 | 400.7656 | 2004-06-04 | 1022.76 | 2004-07-04 | 765.9546 | 2004-08-04 | 907.0679 | 2004-09-04 |  | 2004-10-04 |  | 2004-11-04 | 937.6511 | 2004-12-04 | 974.7711
2004-01-05 | 494.4558 | 2004-02-05 | 513.2923 | 2004-03-05 | 518.7369 | 2004-04-05 | 557.3196 | 2004-05-05 | 431.3293 | 2004-06-05 | 875.1877 | 2004-07-05 | 945.1996 | 2004-08-05 | 983.6426 | 2004-09-05 |  | 2004-10-05 | 1162.5763 | 2004-11-05 | 931.4774 | 2004-12-05 | 925.0961
2004-01-06 | 456.3657 | 2004-02-06 | 499.178 | 2004-03-06 | 504.3138 | 2004-04-06 | 554.6348 | 2004-05-06 |  | 2004-06-06 | 1008.493 | 2004-07-06 | 958.6105 | 2004-08-06 | 969.9464 | 2004-09-06 | 602.9221 | 2004-10-06 | 816.0057 | 2004-11-06 | 984.9656 | 2004-12-06 | 864.3707
2004-01-07 | 452.7417 | 2004-02-07 | 590.0785 | 2004-03-07 | 553.728 | 2004-04-07 | 489.1625 | 2004-05-07 | 329.3854 | 2004-06-07 | 931.5552 | 2004-07-07 | 939.856 | 2004-08-07 | 900.5569 | 2004-09-07 | 948.9868 | 2004-10-07 |  | 2004-11-07 | 1112.9014 | 2004-12-07 | 1086.0275
2004-01-08 | 146.0615 | 2004-02-08 | 585.0459 | 2004-03-08 | 549.3296 | 2004-04-08 | 458.3328 | 2004-05-08 |  | 2004-06-08 | 971.8399 | 2004-07-08 | 885.8749 | 2004-08-08 | 1122.6288 | 2004-09-08 | 883.4885 | 2004-10-08 | 734.5932 | 2004-11-08 | 982.3715 | 2004-12-08 | 1064.4973
2004-01-09 | 471.7886 | 2004-02-09 | 560.1136 | 2004-03-09 | 495.742 | 2004-04-09 | 501.03 | 2004-05-09 |  | 2004-06-09 | 944.3954 | 2004-07-09 | 865.3045 | 2004-08-09 | 894.3313 | 2004-09-09 | 973.8632 | 2004-10-09 | 758.2244 | 2004-11-09 | 915.7578 | 2004-12-09 | 1146.1045
2004-01-10 | 122.8421 | 2004-02-10 | 588.0898 | 2004-03-10 | 513.8557 | 2004-04-10 | 481.4842 | 2004-05-10 |  | 2004-06-10 | 929.8431 | 2004-07-10 | 968.6752 | 2004-08-10 | 967.3004 | 2004-09-10 | 992.6697 | 2004-10-10 | 706.7207 | 2004-11-10 | 1020.0882 | 2004-12-10 | 1046.1837
2004-01-11 | 477.8724 | 2004-02-11 | 540.3266 | 2004-03-11 | 533.5897 | 2004-04-11 | 531.8466 | 2004-05-11 |  | 2004-06-11 | 1016.6122 | 2004-07-11 | 946.0556 | 2004-08-11 | 557.566 | 2004-09-11 | 965.5624 | 2004-10-11 | 780.455 | 2004-11-11 |  | 2004-12-11 | 1273.4176
2004-01-12 | 122.9305 | 2004-02-12 | 583.6225 | 2004-03-12 | 533.5897 | 2004-04-12 | 387.0304 | 2004-05-12 |  | 2004-06-12 | 801.6869 | 2004-07-12 | 932.5928 | 2004-08-12 |  | 2004-09-12 | 1022.4487 | 2004-10-12 | 696.0594 | 2004-11-12 |  | 2004-12-12 | 1010.4904
2004-01-13 | 121.9466 | 2004-02-13 | 470.1379 | 2004-03-13 | 515.7995 | 2004-04-13 | 403.3142 | 2004-05-13 |  | 2004-06-13 | 942.1387 | 2004-07-13 | 946.9116 | 2004-08-13 |  | 2004-09-13 | 987.8708 | 2004-10-13 | 913.9938 | 2004-11-13 |  | 2004-12-13 | 1018.8949
2004-01-14 | 477.3074 | 2004-02-14 | 498.1485 | 2004-03-14 | 531.7218 | 2004-04-14 | 462.7815 | 2004-05-14 |  | 2004-06-14 | 932.93 | 2004-07-14 | 964.1097 | 2004-08-14 |  | 2004-09-14 | 942.2684 | 2004-10-14 | 862.0362 | 2004-11-14 |  | 2004-12-14 | 1088.3621
2004-01-15 | 480.8722 | 2004-02-15 | 463.4484 | 2004-03-15 | 584.8276 | 2004-04-15 | 477.4506 | 2004-05-15 |  | 2004-06-15 | 871.9451 | 2004-07-15 | 923.41 | 2004-08-15 |  | 2004-09-15 | 837.1339 | 2004-10-15 | 805.7205 | 2004-11-15 |  | 2004-12-15 | 1074.9512
2004-01-16 | 476.6529 | 2004-02-16 | 463.4484 | 2004-03-16 | 531.7331 | 2004-04-16 | 477.1523 | 2004-05-16 |  | 2004-06-16 | 996.8979 | 2004-07-16 | 938.5849 | 2004-08-16 | 855.7587 | 2004-09-16 | 978.7659 | 2004-10-16 | 957.5471 | 2004-11-16 |  | 2004-12-16 | 829.8965
2004-01-17 | 149.7807 | 2004-02-17 | 535.2996 | 2004-03-17 | 571.5647 | 2004-04-17 | 486.9965 | 2004-05-17 |  | 2004-06-17 | 1006.366 | 2004-07-17 | 750.1961 | 2004-08-17 | 798.4833 | 2004-09-17 | 944.6289 | 2004-10-17 | 750.2609 | 2004-11-17 | 1056.2744 | 2004-12-17 | 1010.7758
2004-01-18 | -3.7357 | 2004-02-18 | 500.1215 | 2004-03-18 | 554.0836 | 2004-04-18 | 441.3422 | 2004-05-18 |  | 2004-06-18 | 1062.1887 | 2004-07-18 | 920.9197 | 2004-08-18 | 951.8402 | 2004-09-18 | 943.2281 | 2004-10-18 | 773.8533 | 2004-11-18 | 839.7667 | 2004-12-18 | 1004.1611
2004-01-19 | 136.7412 | 2004-02-19 | 596.4557 | 2004-03-19 | 557.6725 | 2004-04-19 | 497.0612 | 2004-05-19 |  | 2004-06-19 | 1054.1215 | 2004-07-19 | 910.9847 | 2004-08-19 |  | 2004-09-19 | 948.2086 | 2004-10-19 | 928.4943 | 2004-11-19 | 1034.6924 | 2004-12-19 | 1045.7688
2004-01-20 | -5.2317 | 2004-02-20 | 705.1659 | 2004-03-20 | 549.8068 | 2004-04-20 | 498.1895 | 2004-05-20 |  | 2004-06-20 | 958.7402 | 2004-07-20 | 929.9988 | 2004-08-20 | 988.2081 | 2004-09-20 | 814.7347 | 2004-10-20 | 741.9991 | 2004-11-20 | 995.2118 | 2004-12-20 | 1193.5486
2004-01-21 | 122.1454 | 2004-02-21 | 576.115 | 2004-03-21 | 550.4456 | 2004-04-21 | 473.7671 | 2004-05-21 | 798.1591 | 2004-06-21 | 995.1859 | 2004-07-21 | 885.2784 | 2004-08-21 | 942.2165 | 2004-09-21 | 824.527 | 2004-10-21 | 1057.8567 | 2004-11-21 | 1003.3569 | 2004-12-21 | 1083.3816
2004-01-22 | -4.933 | 2004-02-22 | 592.3764 | 2004-03-22 | 551.4291 | 2004-04-22 | 345.9934 | 2004-05-22 | 643.9461 | 2004-06-22 | 997.728 | 2004-07-22 | 937.9105 | 2004-08-22 | 1024.939 | 2004-09-22 | 948.0011 | 2004-10-22 | 1000.322 | 2004-11-22 | 993.6554 | 2004-12-22 | 1135.6765
2004-01-23 | 127.1196 | 2004-02-23 | 599.9055 | 2004-03-23 | 540.5316 | 2004-04-23 | 414.877 | 2004-05-23 | 746.5126 | 2004-06-23 | 974.0188 | 2004-07-23 | 891.4261 | 2004-08-23 | 1026.5214 | 2004-09-23 | 931.0105 | 2004-10-23 | 819.0407 | 2004-11-23 | 993.3701 | 2004-12-23 | 1035.4187
2004-01-24 | 166.6929 | 2004-02-24 | 625.5176 | 2004-03-24 | 572.8296 | 2004-04-24 | 413.0806 | 2004-05-24 | 798.4314 | 2004-06-24 | 952.2552 | 2004-07-24 | 931.0623 | 2004-08-24 | 879.8828 | 2004-09-24 | 749.5994 | 2004-10-24 | 869.5069 | 2004-11-24 | 1018.5837 | 2004-12-24 | 1273.8586
2004-01-25 | 188.2551 | 2004-02-25 | 614.9177 | 2004-03-25 | 567.4189 | 2004-04-25 | 420.4022 | 2004-05-25 | 718.718 | 2004-06-25 | 883.7219 | 2004-07-25 | 898.793 | 2004-08-25 | 1001.8265 | 2004-09-25 |  | 2004-10-25 |  | 2004-11-25 | 1013.5773 | 2004-12-25 | 1015.9119
2004-01-26 | 174.2772 | 2004-02-26 | 614.9177 | 2004-03-26 | 553.0039 | 2004-04-26 | 429.6692 | 2004-05-26 | 734.8526 | 2004-06-26 | 1024.7054 | 2004-07-26 | 893.5792 | 2004-08-26 | 958.9218 | 2004-09-26 |  | 2004-10-26 | 1013.3179 | 2004-11-26 | 1006.3141 | 2004-12-26
2004-01-27 | 181.0253 | 2004-02-27 | 576.8603 | 2004-03-27 | 548.1194 | 2004-04-27 | 572.728 | 2004-05-27 | 784.6702 | 2004-06-27 | 942.7353 | 2004-07-27 | 908.754 | 2004-08-27 | 1039.0763 | 2004-09-27 |  | 2004-10-27 | 883.696 | 2004-11-27 | 1031.0089 | 2004-12-27 | 1130.1254
2004-01-28 | 395.9224 | 2004-02-28 | 561.8932 | 2004-03-28 | 585.6947 | 2004-04-28 | 531.6391 | 2004-05-28 | 1030.6458 | 2004-06-28 | 989.8682 | 2004-07-28 | 1102.3696 | 2004-08-28 | 1106.52 | 2004-09-28 |  | 2004-10-28 | 929.1687 | 2004-11-28 | 796.447 | 2004-12-28 | 1057.8567
2004-01-29 | 407.915 | 2004-02-29 | 610.3312 | 2004-03-29 | 572.3724 | 2004-04-29 | 524.9855 | 2004-05-29 | 707.9399 | 2004-06-29 | 787.7182 | 2004-07-29 | 900.09 | 2004-08-29 |  | 2004-09-29 |  | 2004-10-29 | 834.7344 | 2004-11-29 | 888.002 | 2004-12-29 | 1093.161
2004-01-30 | 427.103 |  |  | 2004-03-30 |  | 2004-04-30 | 529.0322 | 2004-05-30 | 861.7767 | 2004-06-30 | 927.1973 | 2004-07-30 | 950.5432 | 2004-08-30 |  | 2004-09-30 |  | 2004-10-30 | 1074.8215 | 2004-11-30 | 907.4051 | 2004-12-30 | 1083.0444
2004-01-31 | 462.5251 |  |  | 2004-03-31 |  |  |  | 2004-05-31 | 643.129 |  |  | 2004-07-31 | 907.016 | 2004-08-31 |  |  |  | 2004-10-31 | 961.2305 |  |  | 2004-12-31 | 1124.4446
Average | 264.1062 |  | 544.8193 |  | 546.8409 |  | 486.8214 |  | 634.7672 |  | 948.7862 |  | 914.78 |  | 937.9866 |  | 907.3641 |  | 873.2894 |  | 994.2362 |  | 1056.2943
Date | FI-2007 | Date | FI-2007 | Date | FI-2007 | Date | FI-2007 | Date | FI-2007 | Date | FI-2007 | Date | FI-2007 | Date | FI-2007 | Date | FI-2007 | Date | FI-2007 | Date | FI-2007 | Date | FI-2007
| Kg/hr |  | Kg/hr |  | Kg/hr |  | Kg/hr |  | Kg/hr |  | Kg/hr |  | Kg/hr |  | Kg/hr |  | Kg/hr |  | Kg/hr |  | Kg/hr |  | Kg/hr
2005-01-01 | 513.7017 | 2005-02-01 | 973.1887 | 2005-03-01 | 1021.3592 | 2005-04-01 | 952.1255 | 2005-05-01 | 1561.403 | 2005-06-01 | 874.7208 | 2005-07-01 | 911.5036 | 2005-08-01 | 937.9623 | 2005-09-01 | 973.1887 | 2005-10-01 | 937.9623 | 2005-11-01 | 911.5036 | 2005-12-01
2005-01-02 | 215.0291 | 2005-02-02 | 1121.4355 | 2005-03-02 | 1281.0699 | 2005-04-02 | 1046.0281 | 2005-05-02 | 1022.1375 | 2005-06-02 | 985.7178 | 2005-07-02 | 926.6006 | 2005-08-02 | 1141.6427 | 2005-09-02 |  | 2005-10-02 | 1141.6427 | 2005-11-02 | 926.6006 | 2005-12-02
2005-01-03 | 215.0291 | 2005-02-03 | 1012.6694 | 2005-03-03 | 941.4642 | 2005-04-03 | 958.4549 | 2005-05-03 | 1383.5845 | 2005-06-03 | 873.7869 | 2005-07-03 | 888.1577 | 2005-08-03 | 1018.9469 | 2005-09-03 |  | 2005-10-03 | 1018.9469 | 2005-11-03 | 888.1577 | 2005-12-03
2005-01-04 | 153.224 | 2005-02-04 | 1024.057 | 2005-03-04 |  | 2005-04-04 | 926.6525 | 2005-05-04 | 788.7558 | 2005-06-04 | 921.8278 | 2005-07-04 | 1204.8065 | 2005-08-04 | 1082.7072 | 2005-09-04 |  | 2005-10-04 | 1082.7072 | 2005-11-04 | 1204.8065 | 2005-12-04
2005-01-05 | 512.1711 | 2005-02-05 | 1082.6553 | 2005-03-05 | 1193.3929 | 2005-04-05 | 1106.8832 | 2005-05-05 | 1065.976 | 2005-06-05 | 1022.5006 | 2005-07-05 | 980.2444 | 2005-08-05 | 991.3467 | 2005-09-05 |  | 2005-10-05 | 991.3467 | 2005-11-05 | 980.2444 | 2005-12-05
2005-01-06 | 573.3635 | 2005-02-06 | 1034.0439 | 2005-03-06 | 1085.2753 | 2005-04-06 | 936.0947 | 2005-05-06 | 757.4852 | 2005-06-06 | 924.3439 | 2005-07-06 | 932.6188 | 2005-08-06 | 874.7208 | 2005-09-06 |  | 2005-10-06 | 1011.3723 | 2005-11-06 | 932.6188 | 2005-12-06 | 921.8278
2005-01-07 | 414.209 | 2005-02-07 | 965.5365 | 2005-03-07 |  | 2005-04-07 | 979.7775 | 2005-05-07 | 963.7207 | 2005-06-07 | 1021.7224 | 2005-07-07 | 937.9623 | 2005-08-07 | 985.7178 | 2005-09-07 | 874.7208 | 2005-10-07 | 1018.5577 | 2005-11-07 | 937.9623 | 2005-12-07 | 1022.5006
2005-01-08 | 143.8175 | 2005-02-08 | 1973.4589 | 2005-03-08 | 1096.5332 | 2005-04-08 | 1005.2505 | 2005-05-08 | 783.2177 | 2005-06-08 | 1016.7419 | 2005-07-08 | 1141.6427 | 2005-08-08 | 873.7869 | 2005-09-08 | 985.7178 | 2005-10-08 | 983.5648 | 2005-11-08 | 1141.6427 | 2005-12-08 | 924.3439
2005-01-09 | 483.0017 | 2005-02-09 | 961.6195 | 2005-03-09 | 1055.6519 | 2005-04-09 | 904.6295 | 2005-05-09 | 1053.9917 | 2005-06-09 | 1106.4941 | 2005-07-09 | 1018.9469 | 2005-08-09 | 921.8278 | 2005-09-09 | 873.7869 | 2005-10-09 | 1062.8113 | 2005-11-09 | 1018.9469 | 2005-12-09 | 1021.7224
2005-01-10 | 131.6549 | 2005-02-10 | 1068.3364 | 2005-03-10 | 1743.2159 | 2005-04-10 | 998.4802 | 2005-05-10 | 1014.2258 | 2005-06-10 | 958.1955 | 2005-07-10 | 1082.7072 | 2005-08-10 | 1022.5006 | 2005-09-10 | 921.8278 | 2005-10-10 | 1091.9418 | 2005-11-10 | 1082.7072 | 2005-12-10 | 1016.7419
2005-01-11 | 497.1001 | 2005-02-11 | 1238.6322 | 2005-03-11 | 1147.2717 | 2005-04-11 | 1033.7844 | 2005-05-11 | 1025.0687 | 2005-06-11 | 1093.2388 | 2005-07-11 | 991.3467 | 2005-08-11 | 924.3439 | 2005-09-11 | 1022.5006 | 2005-10-11 | 874.7208 | 2005-11-11 | 991.3467 | 2005-12-11 | 1106.4941
2005-01-12 | 130.4422 | 2005-02-12 |  | 2005-03-12 | 941.7496 | 2005-04-12 | 1011.3723 | 2005-05-12 | 1069.7373 | 2005-06-12 | 967.6376 | 2005-07-12 | 513.7017 | 2005-08-12 | 1021.7224 | 2005-09-12 | 924.3439 | 2005-10-12 | 985.7178 | 2005-11-12 | 513.7017 | 2005-12-12 | 958.1955
2005-01-13 | 116.292 | 2005-02-13 | 833.4892 | 2005-03-13 | 1383.6624 | 2005-04-13 | 1018.5577 | 2005-05-13 | 995.6788 | 2005-06-13 | 811.4274 | 2005-07-13 | 215.0291 | 2005-08-13 | 1016.7419 | 2005-09-13 | 1021.7224 | 2005-10-13 | 873.7869 | 2005-11-13 | 215.0291 | 2005-12-13 | 513.7017
2005-01-14 | 488.6047 | 2005-02-14 | 986.6776 | 2005-03-14 | 1562.6998 | 2005-04-14 | 983.5648 | 2005-05-14 | 980.8152 | 2005-06-14 | 1038.2202 | 2005-07-14 | 215.0291 | 2005-08-14 | 1106.4941 | 2005-09-14 | 1016.7419 | 2005-10-14 | 921.8278 | 2005-11-14 | 215.0291 | 2005-12-14 | 215.0291
2005-01-15 | 472.2107 | 2005-02-15 | 1012.0987 | 2005-03-15 | 1220.993 | 2005-04-15 | 999.5697 | 2005-05-15 | 911.5036 | 2005-06-15 | 992.4363 | 2005-07-15 | 153.224 | 2005-08-15 | 958.1955 | 2005-09-15 | 1106.4941 | 2005-10-15 | 1022.5006 | 2005-11-15 | 153.224 | 2005-12-15 | 215.0291
2005-01-16 | 488.6436 | 2005-02-16 | 937.9623 | 2005-03-16 | 896.5103 | 2005-04-16 | 1080.7098 | 2005-05-16 | 926.6006 | 2005-06-16 | 1136.5585 | 2005-07-16 | 973.1887 | 2005-08-16 | 911.5036 | 2005-09-16 | 958.1955 | 2005-10-16 | 924.3439 | 2005-11-16 |  | 2005-12-16 | 153.224
2005-01-17 | 187.669 | 2005-02-17 | 1141.6427 | 2005-03-17 | 1048.259 | 2005-04-17 | 752.6474 | 2005-05-17 | 888.1577 | 2005-06-17 | 1048.259 | 2005-07-17 | 874.7208 | 2005-08-17 | 926.6006 | 2005-09-17 |  | 2005-10-17 | 1021.7224 | 2005-11-17 |  | 2005-12-17 | 1226.0254
2005-01-18 |  | 2005-02-18 | 1018.9469 | 2005-03-18 | 1127.2202 | 2005-04-18 |  | 2005-05-18 | 1204.8065 | 2005-06-18 | 1127.2202 | 2005-07-18 | 985.7178 | 2005-08-18 | 888.1577 | 2005-09-18 |  | 2005-10-18 | 1016.7419 | 2005-11-18 |  | 2005-12-18 | 1066.8579
2005-01-19 |  | 2005-02-19 | 1082.7072 | 2005-03-19 | 1076.741 | 2005-04-19 |  | 2005-05-19 | 980.2444 | 2005-06-19 | 1076.741 | 2005-07-19 | 873.7869 | 2005-08-19 | 1204.8065 | 2005-09-19 |  | 2005-10-19 | 1106.4941 | 2005-11-19 | 937.9623 | 2005-12-19 | 989.4791
2005-01-20 |  | 2005-02-20 | 991.3467 | 2005-03-20 | 1036.8972 | 2005-04-20 |  | 2005-05-20 | 932.6188 | 2005-06-20 | 1036.8972 | 2005-07-20 | 921.8278 | 2005-08-20 | 980.2444 | 2005-09-20 |  | 2005-10-20 | 958.1955 | 2005-11-20 | 1141.6427 | 2005-12-20 | 928.5203
2005-01-21 | 962.0087 | 2005-02-21 | 1172.2518 | 2005-03-21 | 1002.1118 | 2005-04-21 |  | 2005-05-21 |  | 2005-06-21 | 1002.1118 | 2005-07-21 | 1022.5006 | 2005-08-21 | 932.6188 | 2005-09-21 |  | 2005-10-21 | 911.5036 | 2005-11-21 | 1018.9469 | 2005-12-21 | 999.1806
2005-01-22 | 1018.7134 | 2005-02-22 | 806.0837 | 2005-03-22 | 962.3199 | 2005-04-22 |  | 2005-05-22 |  | 2005-06-22 | 962.3199 | 2005-07-22 | 924.3439 | 2005-08-22 | 937.9623 | 2005-09-22 |  | 2005-10-22 | 926.6006 | 2005-11-22 | 1082.7072 | 2005-12-22 | 999.1806
2005-01-23 | 959.9594 | 2005-02-23 | 931.5033 | 2005-03-23 | 1005.6136 | 2005-04-23 |  | 2005-05-23 |  | 2005-06-23 | 1005.6136 | 2005-07-23 | 1021.7224 | 2005-08-23 | 1141.6427 | 2005-09-23 |  | 2005-10-23 | 888.1577 | 2005-11-23 | 991.3467 | 2005-12-23 | 923.0988
2005-01-24 | 946.1853 | 2005-02-24 | 1074.1989 | 2005-03-24 | 1088.2583 | 2005-04-24 |  | 2005-05-24 |  | 2005-06-24 | 1088.2583 | 2005-07-24 | 1016.7419 | 2005-08-24 | 1018.9469 | 2005-09-24 |  | 2005-10-24 | 1204.8065 | 2005-11-24 |  | 2005-12-24 | 1361.5615
2005-01-25 | 954.3823 | 2005-02-25 | 1056.5598 | 2005-03-25 | 1038.6611 | 2005-04-25 |  | 2005-05-25 |  | 2005-06-25 | 1038.6611 | 2005-07-25 | 1106.4941 | 2005-08-25 | 1082.7072 | 2005-09-25 |  | 2005-10-25 | 980.2444 | 2005-11-25 |  | 2005-12-25 | 1361.5615
2005-01-26 | 1028.1815 | 2005-02-26 | 1120.4498 | 2005-03-26 | 1119.6458 | 2005-04-26 |  | 2005-05-26 | 945.4849 | 2005-06-26 | 1119.6458 | 2005-07-26 | 958.1955 | 2005-08-26 | 991.3467 | 2005-09-26 |  | 2005-10-26 | 932.6188 | 2005-11-26 |  | 2005-12-26 | 3032.5867
2005-01-27 | 1087.2467 | 2005-02-27 | 981.1264 | 2005-03-27 | 1059.1278 | 2005-04-27 |  | 2005-05-27 | 645.3339 | 2005-06-27 | 1059.1278 | 2005-07-27 | 1011.3723 | 2005-08-27 |  | 2005-09-27 |  | 2005-10-27 | 513.7017 | 2005-11-27 |  | 2005-12-27 | 1089.7888
2005-01-28 | 1097.1299 | 2005-02-28 | 1014.978 | 2005-03-28 | 1029.8157 | 2005-04-28 |  | 2005-05-28 | 822.4907 | 2005-06-28 | 1029.8157 | 2005-07-28 | 1018.5577 | 2005-08-28 |  | 2005-09-28 |  | 2005-10-28 | 215.0291 | 2005-11-28 |  | 2005-12-28 | 1312.587
2005-01-29 | 962.0087 |  |  | 2005-03-29 | 1012.9288 | 2005-04-29 |  | 2005-05-29 | 1067.7399 | 2005-06-29 | 1012.9288 | 2005-07-29 | 983.5648 | 2005-08-29 |  | 2005-09-29 |  | 2005-10-29 | 215.0291 | 2005-11-29 |  | 2005-12-29 | 1312.587
2005-01-30 | 965.5106 |  |  | 2005-03-30 | 1062.8113 | 2005-04-30 |  | 2005-05-30 | 1038.5055 | 2005-06-30 | 1062.8113 | 2005-07-30 | 1062.8113 | 2005-08-30 |  | 2005-09-30 |  | 2005-10-30 | 153.224 | 2005-11-30 |  | 2005-12-30
2005-01-31 | 1063.3042 |  |  | 2005-03-31 | 1091.9418 |  |  | 2005-05-31 | 1013.9405 |  |  | 2005-07-31 | 1091.9418 | 2005-08-31 |  |  |  | 2005-10-31 |  |  | 966.185 | 2005-12-31 | 966.185
Average | 599.3141 |  | 1059.9132 |  | 1114.938 |  | 982.0343 |  | 993.9702 |  | 1013.8661 |  | 901.9681 |  | 995.969 |  | 970.84 |  | 899.594 |  | 864.3064 |  | 1025.5204
Date | FI-2007 | Date | FI-2007 | Date | FI-2007 | Date | FI-2007 | Date | FI-2007 | Date | FI-2007 | Date | FI-2007 | Date | FI-2007 | Date | FI-2007 | Date | FI-2007 | Date | FI-2007 | Date | FI-2007
| Kg/hr |  | Kg/hr |  | Kg/hr |  | Kg/hr |  | Kg/hr |  | Kg/hr |  | Kg/hr |  | Kg/hr |  | Kg/hr |  | Kg/hr |  | Kg/hr |  | Kg/hr
2006-01-01 | 706.4872 | 2006-02-01 | 1025.5615 | 2006-03-01 | 1041.8518 | 2006-04-01 | 1076.5594 | 2006-05-01 |  | 2006-06-01 | 860.7132 | 2006-07-01 | 729.5739 | 2006-08-01 | 677.0325 | 2006-09-01 |  | 2006-10-01 | 740.6501 | 2006-11-01 | 906.1082 | 2006-12-01 | 844.1506
2006-01-02 | 832.8796 | 2006-02-02 | 1080.8914 | 2006-03-02 | 883.5144 | 2006-04-02 | 1187.764 | 2006-05-02 | 568.6165 | 2006-06-02 | 932.8522 | 2006-07-02 | 886.5494 | 2006-08-02 | 730.5076 | 2006-09-02 |  | 2006-10-02 | 952.0737 | 2006-11-02 | 968.2862 | 2006-12-02 | 883.9294
2006-01-03 | 1011.9431 | 2006-02-03 | 998.4283 | 2006-03-03 | 1023.0973 | 2006-04-03 | 1142.1616 | 2006-05-03 | 1218.6843 | 2006-06-03 | 906.9382 | 2006-07-03 | 1122.4731 | 2006-08-03 | 955.4718 | 2006-09-03 |  | 2006-10-03 | 1003.9276 | 2006-11-03 | 940.686 | 2006-12-03 | 993.8889
2006-01-04 | 1073.4725 | 2006-02-04 | 983.9797 | 2006-03-04 | 1078.8682 | 2006-04-04 | 1014.6149 | 2006-05-04 | 906.2897 | 2006-06-04 | 915.654 | 2006-07-04 | 1051.6571 | 2006-08-04 | 827.6527 | 2006-09-04 |  | 2006-10-04 | 1004.0055 | 2006-11-04 | 841.2712 | 2006-12-04 | 991.1133
2006-01-05 | 1004.0833 | 2006-02-05 | 1087.3246 | 2006-03-05 | 1025.5355 | 2006-04-05 | 1168.4647 | 2006-05-05 | 1100.0092 | 2006-06-05 | 917.2104 | 2006-07-05 | 970.8542 | 2006-08-05 | 1160.2417 | 2006-09-05 |  | 2006-10-05 | 674.659 | 2006-11-05 | 1025.4318 | 2006-12-05 | 895.5246
2006-01-06 | 1050.5676 | 2006-02-06 | 994.8487 | 2006-03-06 | 892.8528 | 2006-04-06 | 1096.7407 | 2006-05-06 | 968.9346 | 2006-06-06 | 887.8723 | 2006-07-06 | 822.2703 | 2006-08-06 | 759.8328 | 2006-09-06 |  | 2006-10-06 | 1098.9457 | 2006-11-06 | 885.4858 | 2006-12-06 | 697.979
2006-01-07 | 1106.52 | 2006-02-07 | 1447.0337 | 2006-03-07 | 1148.3352 | 2006-04-07 | 1191.2399 | 2006-05-07 | 847.9378 | 2006-06-07 | 861.1023 | 2006-07-07 | 962.6053 | 2006-08-07 | 750.1442 | 2006-09-07 |  | 2006-10-07 | 1090.4893 | 2006-11-07 | 976.2756 | 2006-12-07 | 1033.6807
2006-01-08 | 1157.9071 | 2006-02-08 | 1197.2321 | 2006-03-08 | 998.5062 | 2006-04-08 | 1007.0404 | 2006-05-08 | 974.5895 | 2006-06-08 | 900.1937 | 2006-07-08 | 2199.9146 | 2006-08-08 | 1054.0696 | 2006-09-08 |  | 2006-10-08 | 731.5063 | 2006-11-08 | 1051.9684 | 2006-12-08 | 854.306
2006-01-09 | 155.5715 | 2006-02-09 | 1159.9304 | 2006-03-09 | 1067.1433 | 2006-04-09 | 1092.0715 | 2006-05-09 | 1016.4826 | 2006-06-09 | 928.598 | 2006-07-09 | 955.4977 | 2006-08-09 |  | 2006-09-09 |  | 2006-10-09 | 731.5063 | 2006-11-09 | 700.1969 | 2006-12-09 | 619.2772
2006-01-10 | 1033.136 | 2006-02-10 | 1081.9808 | 2006-03-10 | 1019.9066 | 2006-04-10 | 724.2951 | 2006-05-10 | 980.6854 | 2006-06-10 | 855.2139 | 2006-07-10 | 661.0016 | 2006-08-10 | 872.5677 | 2006-09-10 |  | 2006-10-10 | 1134.8983 | 2006-11-10 | 840.6616 | 2006-12-10 | 567.1768
2006-01-11 | 1192.0441 | 2006-02-11 | 1079.5426 | 2006-03-11 | 1076.5336 | 2006-04-11 | 1147.7646 | 2006-05-11 | 980.6854 | 2006-06-11 | 922.5021 | 2006-07-11 | 771.0778 | 2006-08-11 | 652.1171 | 2006-09-11 |  | 2006-10-11 | 1207.1411 | 2006-11-11 | 1067.6101 | 2006-12-11 | 823.671
2006-01-12 | 1029.4525 | 2006-02-12 | 1062.5519 | 2006-03-12 | 1159.5154 | 2006-04-12 | 947.0154 | 2006-05-12 | 1005.8472 | 2006-06-12 | 809.4559 | 2006-07-12 | 778.8078 | 2006-08-12 | 991.7877 | 2006-09-12 | 914.5905 | 2006-10-12 | 1088.6993 | 2006-11-12 | 653.8292 | 2006-12-12
2006-01-13 | 1018.2205 | 2006-02-13 | 1066.5466 | 2006-03-13 | 1096.2998 | 2006-04-13 | 1071.5531 | 2006-05-13 | 875.6805 | 2006-06-13 | 893.7347 | 2006-07-13 | 821.6347 | 2006-08-13 |  | 2006-09-13 | 1396.5546 | 2006-10-13 | 940.2451 | 2006-11-13 | 951.1398 | 2006-12-13 | 823.671
2006-01-14 | 1054.2511 | 2006-02-14 | 1066.5466 | 2006-03-14 | 1055.8853 | 2006-04-14 | 1065.0421 | 2006-05-14 | 871.9971 | 2006-06-14 | 866.9128 | 2006-07-14 | 750.5073 | 2006-08-14 | 869.7922 | 2006-09-14 | 908.2611 | 2006-10-14 | 866.4978 | 2006-11-14 | 946.6262 | 2006-12-14 | 1181.72
2006-01-15 | 1053.9917 | 2006-02-15 | 1086.8317 | 2006-03-15 | 689.5226 | 2006-04-15 | 477.4506 | 2006-05-15 |  | 2006-06-15 | 1032.9285 | 2006-07-15 | 923.41 | 2006-08-15 |  | 2006-09-15 | 658.8486 | 2006-10-15 | 1017.4942 | 2006-11-15 | 617.3706 | 2006-12-15 | 967.3264
2006-01-16 | 935.3943 | 2006-02-16 | 1177.3361 | 2006-03-16 | 973.6298 | 2006-04-16 |  | 2006-05-16 | 892.2562 | 2006-06-16 | 928.2608 | 2006-07-16 | 886.5494 | 2006-08-16 | 724.6453 | 2006-09-16 | 939.8819 | 2006-10-16 | 1116.7922 | 2006-11-16 | 908.8318 | 2006-12-16 | 986.5739
2006-01-17 | 1003.9796 | 2006-02-17 | 1124.9115 | 2006-03-17 | 1160.2936 | 2006-04-17 |  | 2006-05-17 | 878.2227 | 2006-06-17 | 927.9755 | 2006-07-17 | 964.7842 | 2006-08-17 | 679.3281 | 2006-09-17 | 861.4395 | 2006-10-17 | 894.072 | 2006-11-17 | 989.116 | 2006-12-17 | 849.4812
2006-01-18 | 1113.1606 | 2006-02-18 | 1108.9844 | 2006-03-18 | 1062.8372 | 2006-04-18 |  | 2006-05-18 | 834.2933 | 2006-06-18 | 888.5208 | 2006-07-18 | 696.669 | 2006-08-18 | 965.8997 | 2006-09-18 | 504.6486 | 2006-10-18 | 1080.684 | 2006-11-18 | 897.522 | 2006-12-18 | 523.2735
2006-01-19 | 1166.6488 | 2006-02-19 | 1133.1604 | 2006-03-19 | 1078.064 | 2006-04-19 |  | 2006-05-19 | 966.4444 | 2006-06-19 | 878.8712 | 2006-07-19 | 684.2048 | 2006-08-19 | 740.0666 | 2006-09-19 | 1198.6847 | 2006-10-19 | 961.5676 | 2006-11-19 | 998.7396 | 2006-12-19 | 387.3028
2006-01-20 | 1005.0949 | 2006-02-20 | 1362.5732 | 2006-03-20 | 1207.2449 | 2006-04-20 | 234.9316 | 2006-05-20 | 962.5016 | 2006-06-20 | 773.4253 | 2006-07-20 | 858.7678 | 2006-08-20 | 764.9689 | 2006-09-20 | 986.7813 | 2006-10-20 | 1054.0177 | 2006-11-20 | 1195.0272 | 2006-12-20 | 1057.1564
2006-01-21 | 1091.6824 | 2006-02-21 | 1194.7158 | 2006-03-21 | 1052.7206 | 2006-04-21 | 237.2337 | 2006-05-21 | 959.0515 | 2006-06-21 | 901.7502 | 2006-07-21 | 906.7566 | 2006-08-21 | 684.4643 | 2006-09-21 | 1081.2805 | 2006-10-21 | 1089.6592 | 2006-11-21 | 906.8604 | 2006-12-21 | 651.8188
2006-01-22 | 1062.7853 | 2006-02-22 | 1073.3688 | 2006-03-22 | 1003.5645 | 2006-04-22 | 237.9341 | 2006-05-22 | 959.0515 | 2006-06-22 | 875.914 | 2006-07-22 | 1056.897 | 2006-08-22 | 683.6213 | 2006-09-22 | 901.0238 | 2006-10-22 | 977.2614 | 2006-11-22 | 886.6791 | 2006-12-22 | 861.6211
2006-01-23 | 1053.8879 | 2006-02-23 | 948.9349 | 2006-03-23 | 1089.0106 | 2006-04-23 | 239.8991 | 2006-05-23 | 903.0731 | 2006-06-23 | 906.8344 | 2006-07-23 | 981.2302 | 2006-08-23 | 683.6213 | 2006-09-23 | 855.8105 | 2006-10-23 | 985.4065 | 2006-11-23 | 948.8831 | 2006-12-23 | 803.5027
2006-01-24 | 217.5129 | 2006-02-24 | 1015.9378 | 2006-03-24 | 1140.657 | 2006-04-24 | 236.916 | 2006-05-24 | 919.3375 | 2006-06-24 | 827.1339 | 2006-07-24 |  | 2006-08-24 | 830.8304 | 2006-09-24 | 956.8466 | 2006-10-24 | 745.942 | 2006-11-24 | 833.593 | 2006-12-24 | 832.9704
2006-01-25 | 1036.0413 | 2006-02-25 | 1094.873 | 2006-03-25 | 999.4141 | 2006-04-25 | 237.0846 | 2006-05-25 | 787.0178 | 2006-06-25 | 937.9105 | 2006-07-25 |  | 2006-08-25 | 731.6749 | 2006-09-25 | 1062.111 | 2006-10-25 | 961.9568 | 2006-11-25 | 833.5151 | 2006-12-25 | 932.2556
2006-01-26 | 892.8528 | 2006-02-26 | 964.6286 | 2006-03-26 | 1037.1307 | 2006-04-26 | 237.6682 | 2006-05-26 | 774.0868 | 2006-06-26 | 872.2565 | 2006-07-26 | 923.2803 | 2006-08-26 | 655.9952 | 2006-09-26 | 1053.7323 | 2006-10-26 | 920.816 | 2006-11-26 | 1029.4265 | 2006-12-26 | 1114.9506
2006-01-27 | 1118.8676 | 2006-02-27 | 1308.3846 | 2006-03-27 | 1095.5475 | 2006-04-27 |  | 2006-05-27 | 963.6948 | 2006-06-27 | 962.8128 | 2006-07-27 | 801.3237 | 2006-08-27 | 755.1506 | 2006-09-27 | 963.6948 | 2006-10-27 | 538.9542 | 2006-11-27 | 869.429 | 2006-12-27 | 509.8495
2006-01-28 | 1022.0078 | 2006-02-28 | 1127.5314 | 2006-03-28 | 1076.6372 | 2006-04-28 |  | 2006-05-28 | 809.0408 | 2006-06-28 | 844.7861 | 2006-07-28 | 897.2366 | 2006-08-28 | 751.493 | 2006-09-28 | 553.7529 | 2006-10-28 | 991.9952 | 2006-11-28 | 1008.6746 | 2006-12-28 | 890.8035
2006-01-29 | 1006.781 |  |  | 2006-03-29 | 1157.0511 | 2006-04-29 | 144.0412 | 2006-05-29 | 921.1533 | 2006-06-29 | 845.0714 | 2006-07-29 | 764.4501 | 2006-08-29 | 746.4866 | 2006-09-29 | 869.5847 | 2006-10-29 | 793.1266 | 2006-11-29 | 992.1768 | 2006-12-29 | 977.6764
2006-01-30 | 1170.5139 |  |  | 2006-03-30 | 1182.8613 | 2006-04-30 | 131.3047 | 2006-05-30 | 942.009 | 2006-06-30 | 869.5328 | 2006-07-30 | 929.2725 | 2006-08-30 | 563.1172 | 2006-09-30 | 954.7974 | 2006-10-30 | 999.051 | 2006-11-30 | 980.6076 | 2006-12-30 | 966.8076
2006-01-31 | 1084.8083 |  |  | 2006-03-31 | 1251.8875 |  |  | 2006-05-31 | 853.1906 |  |  | 2006-07-31 | 828.3272 | 2006-08-31 |  |  |  | 2006-10-31 | 838.4048 |  |  | 2006-12-31 | 887.4573
| 982.6628 |  | 1109.0918 |  | 1058.9006 |  | 748.4994 |  | 918.6505 |  | 891.0979 |  | 916.8132 |  | 787.503 |  | 927.4908 |  | 942.9821 |  | 921.7343 |  | 847.0305
Date | FI-2007 | Date | FI-2007 | Date | FI-2007 | Date | FI-2007 | Date | FI-2007 | Date | FI-2007 | Date | FI-2007 | Date | FI-2007 | Date | FI-2007 | Date | FI-2007 | Date | FI-2007 | Date | FI-2007
| Kg/hr |  | Kg/hr |  | Kg/hr |  | Kg/hr |  | Kg/hr |  | Kg/hr |  | Kg/hr |  | Kg/hr |  | Kg/hr |  | Kg/hr |  | Kg/hr |  | Kg/hr
2007-01-01 | 714.7361 | 2007-02-01 | 990.5426 | 2007-03-01 | 948.6755 | 2007-04-01 | 1031.0348 | 2007-05-01 | 1005.1727 | 2007-06-01 |  | 2007-07-01 | 878.6637 | 2007-08-01 | 788.9893 | 2007-09-01 | 966.0034 | 2007-10-01 | 938.9481 | 2007-11-01 | 1010.9314 | 2007-12-01
2007-01-02 | 215.0291 | 2007-02-02 | 1043.4601 | 2007-03-02 | 1034.7703 | 2007-04-02 | 1060.9695 | 2007-05-02 | 1080.8395 | 2007-06-02 |  | 2007-07-02 | 954.4861 | 2007-08-02 | 772.5823 | 2007-09-02 | 1089.5554 | 2007-10-02 | 753.5812 | 2007-11-02 | 829.9874 | 2007-12-02
2007-01-03 | 215.0291 | 2007-02-03 | 944.3436 | 2007-03-03 | 930.777 | 2007-04-03 | 1140.9943 | 2007-05-03 | 1169.5801 | 2007-06-03 |  | 2007-07-03 | 959.4925 | 2007-08-03 | 904.448 | 2007-09-03 | 909.169 | 2007-10-03 | 713.0112 | 2007-11-03 | 1002.5269 | 2007-12-03 | 987.6892
2007-01-04 | 153.224 | 2007-02-04 | 995.9641 | 2007-03-04 | 924.733 | 2007-04-04 | 1017.5461 | 2007-05-04 | 1069.5038 | 2007-06-04 |  | 2007-07-04 | 975.0046 | 2007-08-04 | 775.3448 | 2007-09-04 | 688.9648 | 2007-10-04 | 1076.1703 | 2007-11-04 | 1047.0657 | 2007-12-04 | 1031.6056
2007-01-05 | 512.1711 | 2007-02-05 | 931.2698 | 2007-03-05 |  | 2007-04-05 | 1001.9302 | 2007-05-05 |  | 2007-06-05 |  | 2007-07-05 | 788.4705 | 2007-08-05 | 1003.6163 | 2007-09-05 | 660.0937 | 2007-10-05 | 693.1801 | 2007-11-05 | 1083.4595 | 2007-12-05 | 1105.1971
2007-01-06 | 573.3635 | 2007-02-06 | 770.3773 | 2007-03-06 | 990.1276 | 2007-04-06 | 1081.6177 | 2007-05-06 |  | 2007-06-06 |  | 2007-07-06 | 885.9009 | 2007-08-06 | 928.7796 | 2007-09-06 | 732.2197 | 2007-10-06 | 1168.5685 | 2007-11-06 | 629.2122 | 2007-12-06 | 1034.2255
2007-01-07 | 414.209 | 2007-02-07 | 1190.1764 | 2007-03-07 | 914.383 | 2007-04-07 | 1115.1321 | 2007-05-07 |  | 2007-06-07 |  | 2007-07-07 | 998.1429 | 2007-08-07 | 811.7645 | 2007-09-07 | 849.1829 | 2007-10-07 | 1161.7981 | 2007-11-07 |  | 2007-12-07 | 264.5355
2007-01-08 | 143.8175 | 2007-02-08 | 1030.7755 | 2007-03-08 | 966.9632 | 2007-04-08 | 1182.7057 | 2007-05-08 | 1048.4664 | 2007-06-08 |  | 2007-07-08 | 865.1489 | 2007-08-08 | 784.1255 | 2007-09-08 | 1046.7544 | 2007-10-08 | 933.812 | 2007-11-08 | 748.3414 | 2007-12-08 | 9.7595
2007-01-09 | 483.0017 | 2007-02-09 | 931.192 | 2007-03-09 | 926.4709 | 2007-04-09 | 1165.1444 | 2007-05-09 | 995.1859 | 2007-06-09 | 741.1301 | 2007-07-09 | 899.649 | 2007-08-09 | 811.2846 | 2007-09-09 | 917.8589 | 2007-10-09 | 928.2089 | 2007-11-09 | 856.6666 | 2007-12-09 | 985.1471
2007-01-10 | 131.6549 | 2007-02-10 | 953.9673 | 2007-03-10 | 1040.8921 | 2007-04-10 | 1076.5854 | 2007-05-10 | 1110.5149 | 2007-06-10 | 620.1981 | 2007-07-10 | 919.96 | 2007-08-10 | 715.0215 | 2007-09-10 | 1150.2808 | 2007-10-10 | 1285.0128 | 2007-11-10 | 718.8606 | 2007-12-10 | 932.0999
2007-01-11 | 497.1001 | 2007-02-11 | 955.1865 | 2007-03-11 | 1030.6199 | 2007-04-11 | 1166.182 | 2007-05-11 | 1006.8329 | 2007-06-11 | 875.4211 | 2007-07-11 | 850.2853 | 2007-08-11 | 739.1456 | 2007-09-11 | 726.3313 | 2007-10-11 | 992.7734 | 2007-11-11 | 933.4229 | 2007-12-11 | 1106.4164
2007-01-12 | 130.4422 | 2007-02-12 | 879.3381 | 2007-03-12 | 1039.3616 | 2007-04-12 | 1028.9856 | 2007-05-12 | 1098.764 | 2007-06-12 | 941.5421 | 2007-07-12 | 913.8123 | 2007-08-12 | 738.5491 | 2007-09-12 | 836.7188 | 2007-10-12 | 731.5452 | 2007-11-12 | 859.7534 | 2007-12-12 | 1021.7743
2007-01-13 | 116.292 | 2007-02-13 | 1003.5645 | 2007-03-13 | 1043.0969 | 2007-04-13 | 1032.1243 | 2007-05-13 | 1050.1785 | 2007-06-13 | 1034.4589 | 2007-07-13 | 1017.3904 | 2007-08-13 | 871.2189 | 2007-09-13 | 928.8574 | 2007-10-13 | 1127.298 | 2007-11-13 | 883.6182 | 2007-12-13 | 1031.1385
2007-01-14 | 488.6047 | 2007-02-14 | 947.3007 | 2007-03-14 | 1024.0051 | 2007-04-14 | 1028.2853 | 2007-05-14 | 1098.8938 | 2007-06-14 | 879.8569 | 2007-07-14 | 1248.5153 | 2007-08-14 | 879.8828 | 2007-09-14 | 960.6598 | 2007-10-14 | 822.8409 | 2007-11-14 | 913.0859 | 2007-12-14 | 1029.271
2007-01-15 | 472.2107 | 2007-02-15 | 1009.9197 | 2007-03-15 | 1054.7959 | 2007-04-15 | 1083.1742 | 2007-05-15 | 1041.5924 | 2007-06-15 | 926.7043 | 2007-07-15 | 724.8398 | 2007-08-15 | 759.9625 | 2007-09-15 | 740.0925 | 2007-10-15 | 1238.1394 | 2007-11-15 | 942.7094 | 2007-12-15 | 1059.2056
2007-01-16 | 488.6436 | 2007-02-16 | 937.9623 | 2007-03-16 | 997.0016 | 2007-04-16 | 994.9006 | 2007-05-16 | 1069.7892 | 2007-06-16 | 804.8386 | 2007-07-16 | 1047.818 | 2007-08-16 | 598.6549 | 2007-09-16 | 994.3817 | 2007-10-16 | 890.1031 | 2007-11-16 | 709.185 | 2007-12-16 | 1053.2135
2007-01-17 | 187.669 | 2007-02-17 | 933.8638 | 2007-03-17 | 989.2197 | 2007-04-17 | 1125.5859 | 2007-05-17 | 1103.2257 | 2007-06-17 |  | 2007-07-17 | 1000.1404 | 2007-08-17 | 619.783 | 2007-09-17 | 797.8737 | 2007-10-17 | 1208.075 | 2007-11-17 |  | 2007-12-17 | 1008.3633
2007-01-18 |  | 2007-02-18 | 891.867 | 2007-03-18 | 983.02 | 2007-04-18 | 1092.3051 | 2007-05-18 | 1083.1223 | 2007-06-18 |  | 2007-07-18 | 980.7633 | 2007-08-18 | 709.8076 | 2007-09-18 | 716.0721 | 2007-10-18 | 1268.6707 | 2007-11-18 | 726.7853 | 2007-12-18 | 903.7476
2007-01-19 | 126.5448 | 2007-02-19 | 907.1976 | 2007-03-19 | 1020.9183 | 2007-04-19 | 1046.2356 | 2007-05-19 | 1089.9703 | 2007-06-19 | 956.3019 | 2007-07-19 | 1099.9573 | 2007-08-19 | 736.007 | 2007-09-19 | 650.4959 | 2007-10-19 | 797.6143 | 2007-11-19 | 848.6511 | 2007-12-19 | 1019.699
2007-01-20 |  | 2007-02-20 | 915.239 | 2007-03-20 | 995.6008 | 2007-04-20 | 993.5516 | 2007-05-20 | 1030.9052 | 2007-06-20 |  | 2007-07-20 | 968.7271 | 2007-08-20 | 636.657 | 2007-09-20 | 953.6041 | 2007-10-20 | 1138.6597 | 2007-11-20 | 833.2299 | 2007-12-20 | 995.2896
2007-01-21 | 134.9915 | 2007-02-21 | 908.1314 | 2007-03-21 | 948.053 | 2007-04-21 | 909.61 | 2007-05-21 | 991.1652 | 2007-06-21 |  | 2007-07-21 | 884.0332 | 2007-08-21 | 690.5731 | 2007-09-21 | 620.1721 | 2007-10-21 | 1274.4812 | 2007-11-21 | 735.7216 | 2007-12-21 | 912.9303
2007-01-22 |  | 2007-02-22 | 1057.1045 | 2007-03-22 | 1092.2791 | 2007-04-22 | 1672.5554 | 2007-05-22 | 1067.7139 | 2007-06-22 |  | 2007-07-22 | 1038.2721 | 2007-08-22 | 645.736 | 2007-09-22 | 788.8206 | 2007-10-22 | 1027.3773 | 2007-11-22 |  | 2007-12-22 | 714.1136
2007-01-23 | 123.0429 | 2007-02-23 | 1014.1998 | 2007-03-23 | 985.8994 | 2007-04-23 | 992.7216 | 2007-05-23 | 1183.9248 | 2007-06-23 | 899.0005 | 2007-07-23 | 981.3339 | 2007-08-23 | 925.1481 | 2007-09-23 | 720.1188 | 2007-10-23 | 1133.6792 | 2007-11-23 |  | 2007-12-23 | 827.3156
2007-01-24 | 138.5161 | 2007-02-24 | 959.2332 | 2007-03-24 | 1089.1144 | 2007-04-24 | 1054.5364 | 2007-05-24 | 1020.166 | 2007-06-24 | 1086.4945 | 2007-07-24 | 885.9528 | 2007-08-24 | 763.9313 | 2007-09-24 | 697.7715 | 2007-10-24 | 1062.9669 | 2007-11-24 |  | 2007-12-24
2007-01-25 | 204.0728 | 2007-02-25 | 919.2336 | 2007-03-25 | 1039.9323 | 2007-04-25 | 1293.2098 | 2007-05-25 | 1014.5111 | 2007-06-25 | 1015.834 | 2007-07-25 | 887.1201 | 2007-08-25 | 673.2322 | 2007-09-25 | 817.4713 | 2007-10-25 | 851.4526 | 2007-11-25 | 948.8831 | 2007-12-25 | 848.2361
2007-01-26 | 171.3852 | 2007-02-26 | 992.1249 | 2007-03-26 | 1106.5979 | 2007-04-26 | 1102.0844 | 2007-05-26 | 1092.4347 | 2007-06-26 | 987.0407 | 2007-07-26 | 727.2781 | 2007-08-26 | 825.837 | 2007-09-26 | 901.5167 | 2007-10-26 |  | 2007-11-26 |  | 2007-12-26 | 723.6725
2007-01-27 | 178.7165 | 2007-02-27 | 1000.7371 | 2007-03-27 | 1066.9357 | 2007-04-27 | 1027.8961 | 2007-05-27 | 1069.2444 | 2007-06-27 | 832.724 | 2007-07-27 | 808.1978 | 2007-08-27 | 796.8491 | 2007-09-27 | 820.8435 | 2007-10-27 | 1009.4269 | 2007-11-27 |  | 2007-12-27 | 834.2545
2007-01-28 | 305.4752 | 2007-02-28 | 964.6545 | 2007-03-28 | 1113.42 | 2007-04-28 | 1075.8071 | 2007-05-28 | 1031.9946 | 2007-06-28 | 938.5071 | 2007-07-28 | 944.4473 | 2007-08-28 | 880.9723 | 2007-09-28 |  | 2007-10-28 | 958.429 | 2007-11-28 |  | 2007-12-28 | 489.6942
2007-01-29 | 410.7071 |  |  | 2007-03-29 | 1022.4747 | 2007-04-29 | 922.3984 | 2007-05-29 | 276.844 | 2007-06-29 | 982.6569 | 2007-07-29 | 759.5474 | 2007-08-29 | 1197.5433 | 2007-09-29 | 820.8435 | 2007-10-29 | 944.3695 | 2007-11-29 |  | 2007-12-29 | 766.9403
2007-01-30 | 394.7735 |  |  | 2007-03-30 | 1034.5886 | 2007-04-30 | 968.7271 | 2007-05-30 |  | 2007-06-30 | 972.9813 | 2007-07-30 |  | 2007-08-30 | 683.5953 | 2007-09-30 | 851.6861 | 2007-10-30 | 1031.0348 | 2007-11-30 |  | 2007-12-30 | 1100.5021
2007-01-31 | 351.1879 |  |  | 2007-03-31 | 1031.0348 |  |  | 2007-05-31 |  |  |  | 2007-07-31 | 909.5062 | 2007-08-31 | 914.6423 |  |  | 2007-10-31 | 1056.1188 |  |  | 2007-12-31 | 811.2068
| 302.7361 |  | 963.5331 |  | 1012.8587 |  | 1082.8179 |  | 1034.636 |  | 911.5112 |  | 926.7619 |  | 793.0221 |  | 839.8074 |  | 1007.2449 |  | 863.1049 |  | 878.8301
Note on AH43: barlianal: Data of July ~ Nov 2005 is lost, due to TPSDDE problem

## Steam Generate from SRU
Steam Generation from SRU, read by FI-5091
Data is taken from TPSDDE (Automatic DCS data) at 08:00 AM
Date | FI-2007 | Date | FI-2007 | Date | FI-2007 | Date | FI-5091 | Date | FI-5091 | Date | FI-5091 | Date | FI-5091 | Date | FI-5091 | Date | FI-5091 | Date | FI-5091 | Date | FI-5091 | Date | FI-5091
| Kg/hr |  | Kg/hr |  | Kg/hr |  | Kg/hr |  | Kg/hr |  | Kg/hr |  | Kg/hr |  | Kg/hr |  | Kg/hr |  | Kg/hr |  | Kg/hr |  | Kg/hr
2004-01-01 | 10554.7181 | 2004-02-01 | 8364.8428 | 2004-03-01 | 12405.8175 | 2004-04-01 | 12367.4463 | 2004-05-01 | 11404.8135 | 2004-06-01 | 12577.5869 | 2004-07-01 | 12699.6562 | 2004-08-01 | 11914.7158 | 2004-09-01 |  | 2004-10-01 |  | 2004-11-01 | 9783.8066 | 2004-12-01 | 9654.6025
2004-01-02 | 10345.156 | 2004-02-02 | 10283.1567 | 2004-03-02 | 12405.8175 | 2004-04-02 | 12237.6543 | 2004-05-02 | 11644.3115 | 2004-06-02 | 12441.6123 | 2004-07-02 | 12532.7773 | 2004-08-02 | 11502.1582 | 2004-09-02 |  | 2004-10-02 |  | 2004-11-02 | 9444.9873 | 2004-12-02 | 9403.6816
2004-01-03 | 0 | 2004-02-03 | 11983.9894 | 2004-03-03 | 12405.8175 | 2004-04-03 | 13106.0303 | 2004-05-03 | 11438.8066 | 2004-06-03 | 12435.4336 | 2004-07-03 | 11590.2324 | 2004-08-03 | 11849.8184 | 2004-09-03 |  | 2004-10-03 |  | 2004-11-03 |  | 2004-12-03 | 9476.6113
2004-01-04 | 9504.1391 | 2004-02-04 | 12006.0134 | 2004-03-04 | 12405.8175 | 2004-04-04 | 12549.7744 | 2004-05-04 | 11959.5254 | 2004-06-04 | 12852.626 | 2004-07-04 | 12117.1299 | 2004-08-04 | 11690.668 | 2004-09-04 |  | 2004-10-04 |  | 2004-11-04 | 9860.25 | 2004-12-04 | 9848.3926
2004-01-05 | 10533.4076 | 2004-02-05 | 11918.6421 | 2004-03-05 | 12240.8719 | 2004-04-05 | 12827.9023 | 2004-05-05 | 11655.1279 | 2004-06-05 | 12554.4092 | 2004-07-05 | 11673.6709 | 2004-08-05 | 11360.0039 | 2004-09-05 |  | 2004-10-05 |  | 2004-11-05 | 9696.7197 | 2004-12-05 | 9558.1377
2004-01-06 | 10039.6653 | 2004-02-06 | 12353.1536 | 2004-03-06 | 12337.5088 | 2004-04-06 | 12318 | 2004-05-06 |  | 2004-06-06 | 12284.0078 | 2004-07-06 | 11954.8877 | 2004-08-06 | 11466.6191 | 2004-09-06 |  | 2004-10-06 | 9266.3145 | 2004-11-06 | 9591.3711 | 2004-12-06 | 9574.7119
2004-01-07 | 10454.0253 | 2004-02-07 | 12182.0271 | 2004-03-07 | 12395.1948 | 2004-04-07 | 10678.5889 | 2004-05-07 |  | 2004-06-07 | 12650.21 | 2004-07-07 | 11639.6768 | 2004-08-07 | 11505.248 | 2004-09-07 | 11709.208 | 2004-10-07 |  | 2004-11-07 | 9871.0674 | 2004-12-07 | 10070.1377
2004-01-08 | 9549.142 | 2004-02-08 | 12316.327 | 2004-03-08 | 12410.1311 | 2004-04-08 | 10896.4551 | 2004-05-08 |  | 2004-06-08 | 12540.5039 | 2004-07-08 | 11863.7246 | 2004-08-08 | 11630.4053 | 2004-09-08 | 11366.1836 | 2004-10-08 | 9881.2861 | 2004-11-08 | 9669.3672 | 2004-12-08 | 9805.1992
2004-01-09 | 10629.0792 | 2004-02-09 | 12188.5935 | 2004-03-09 | 12534.3875 | 2004-04-09 | 11353.8223 | 2004-05-09 |  | 2004-06-09 | 12472.5176 | 2004-07-09 | 11543.876 | 2004-08-09 | 11584.0508 | 2004-09-09 | 12407.6211 | 2004-10-09 | 10232.0381 | 2004-11-09 | 9792.7783 | 2004-12-09 | 9926.8818
2004-01-10 | 9630.134 | 2004-02-10 | 12233.7257 | 2004-03-10 | 12511.2103 | 2004-04-10 | 11406.3574 | 2004-05-10 |  | 2004-06-10 | 12661.0273 | 2004-07-10 | 12163.4854 | 2004-08-10 | 10911.9062 | 2004-09-10 | 12475.6074 | 2004-10-10 | 10134.6924 | 2004-11-10 | 9485.8125 | 2004-12-10 | 9470.2607
2004-01-11 | 10558.6454 | 2004-02-11 | 12336.9935 | 2004-03-11 | 12224.2619 | 2004-04-11 | 11690.668 | 2004-05-11 |  | 2004-06-11 | 12718.1973 | 2004-07-11 | 12146.4893 | 2004-08-11 | 13345.5312 | 2004-09-11 | 12353.54 | 2004-10-11 | 10190.3184 | 2004-11-11 |  | 2004-12-11 | 9764.9053
2004-01-12 | 9540.6436 | 2004-02-12 | 12233.1466 | 2004-03-12 | 12224.2619 | 2004-04-12 | 12209.8398 | 2004-05-12 |  | 2004-06-12 | 12562.1367 | 2004-07-12 | 11893.082 | 2004-08-12 |  | 2004-09-12 | 12440.0684 | 2004-10-12 | 10134.6924 | 2004-11-12 |  | 2004-12-12 | 9547.3887
2004-01-13 | 9547.0818 | 2004-02-13 | 12181.6407 | 2004-03-13 | 12340.3416 | 2004-04-13 | 11877.6309 | 2004-05-13 |  | 2004-06-13 | 12549.7744 | 2004-07-13 | 12095.498 | 2004-08-13 |  | 2004-09-13 | 12395.2598 | 2004-10-13 | 10465.3564 | 2004-11-13 |  | 2004-12-13 | 9752.6309
2004-01-14 | 10531.7983 | 2004-02-14 | 12216.9862 | 2004-03-14 | 12261.9892 | 2004-04-14 | 12165.0303 | 2004-05-14 |  | 2004-06-14 | 12983.9648 | 2004-07-14 | 12100.1348 | 2004-08-14 |  | 2004-09-14 | 12341.1777 | 2004-10-14 | 10457.6309 | 2004-11-14 |  | 2004-12-14 | 9134.3086
2004-01-15 | 10490.2076 | 2004-02-15 | 12219.8839 | 2004-03-15 | 12407.9421 | 2004-04-15 | 11945.6191 | 2004-05-15 |  | 2004-06-15 | 12786.1855 | 2004-07-15 | 11942.5273 | 2004-08-15 |  | 2004-09-15 | 12321.0918 | 2004-10-15 | 10194.9541 | 2004-11-15 |  | 2004-12-15 | 9582.7471
2004-01-16 | 10527.9997 | 2004-02-16 | 12219.8839 | 2004-03-16 | 12379.4211 | 2004-04-16 | 12373.6279 | 2004-05-16 |  | 2004-06-16 | 12713.5625 | 2004-07-16 | 12166.5742 | 2004-08-16 | 10726.4883 | 2004-09-16 | 12188.207 | 2004-10-16 | 10204.2246 | 2004-11-16 |  | 2004-12-16 | 9745.8496
2004-01-17 | 9350.3316 | 2004-02-17 | 12273.1274 | 2004-03-17 | 12359.9138 | 2004-04-17 | 11919.3506 | 2004-05-17 |  | 2004-06-17 | 12679.5684 | 2004-07-17 | 12032.1475 | 2004-08-17 | 11118.959 | 2004-09-17 | 12027.5117 | 2004-10-17 | 10219.6768 | 2004-11-17 | 9906.1816 | 2004-12-17 | 9713.4072
2004-01-18 | 13.2094 | 2004-02-18 | 11982.2512 | 2004-03-18 | 12399.7014 | 2004-04-18 | 12012.0605 | 2004-05-18 |  | 2004-06-18 | 12753.7354 | 2004-07-18 | 12293.2803 | 2004-08-18 | 11282.7441 | 2004-09-18 | 12328.8164 | 2004-10-18 | 10556.5215 | 2004-11-18 | 10048.7705 | 2004-12-18 | 9574.7334
2004-01-19 | 9547.0817 | 2004-02-19 | 12043.285 | 2004-03-19 | 12470.7786 | 2004-04-19 | 12291.7334 | 2004-05-19 |  | 2004-06-19 | 12678.0225 | 2004-07-19 | 12195.9336 | 2004-08-19 |  | 2004-09-19 | 10607.5107 | 2004-10-19 | 10731.123 | 2004-11-19 | 10065.7324 | 2004-12-19 | 9736.3135
2004-01-20 |  | 2004-02-20 | 12130.3288 | 2004-03-20 | 12441.8067 | 2004-04-20 | 12019.7852 | 2004-05-20 |  | 2004-06-20 | 12534.3223 | 2004-07-20 | 12149.5791 | 2004-08-20 | 11800.373 | 2004-09-20 | 10703.3115 | 2004-10-20 | 10222.7666 | 2004-11-20 | 9866.6709 | 2004-12-20 | 9701.4404
2004-01-21 | 9550.7571 | 2004-02-21 | 12231.2146 | 2004-03-21 | 12638.4285 | 2004-04-21 | 11729.2959 | 2004-05-21 | 9427.0107 | 2004-06-21 | 12532.7773 | 2004-07-21 | 12053.7793 | 2004-08-21 | 11801.918 | 2004-09-21 | 10894.9111 | 2004-10-21 | 10330.9277 | 2004-11-21 | 10148.835 | 2004-12-21 | 9567.0107
2004-01-22 |  | 2004-02-22 | 12098.9107 | 2004-03-22 | 12548.4873 | 2004-04-22 | 11384.7256 | 2004-05-22 | 9918.3701 | 2004-06-22 | 12693.4756 | 2004-07-22 | 11786.4668 | 2004-08-22 | 11812.7344 | 2004-09-22 | 10984.5293 | 2004-10-22 | 10700.2207 | 2004-11-22 | 10054.5332 | 2004-12-22 | 9758.9648
2004-01-23 | 9499.8901 | 2004-02-23 | 11934.0937 | 2004-03-23 | 12524.988 | 2004-04-23 | 11919.3506 | 2004-05-23 | 11060.2422 | 2004-06-23 | 12704.291 | 2004-07-23 | 12101.6787 | 2004-08-23 | 11812.7344 | 2004-09-23 | 10947.4453 | 2004-10-23 | 10541.0693 | 2004-11-23 | 9778.1484 | 2004-12-23 | 9968.832
2004-01-24 | 9487.7219 | 2004-02-24 | 12226.4509 | 2004-03-24 | 12502.0037 | 2004-04-24 | 11936.3477 | 2004-05-24 | 11118.959 | 2004-06-24 | 12800.0889 | 2004-07-24 | 12199.0234 | 2004-08-24 | 11761.7461 | 2004-09-24 | 10269.1221 | 2004-10-24 | 10633.7783 | 2004-11-24 | 10030.7686 | 2004-12-24 | 9906.5381
2004-01-25 | 9528.5398 | 2004-02-25 | 11965.1898 | 2004-03-25 | 12456.7434 | 2004-04-25 | 12182.0273 | 2004-05-25 | 11163.7686 | 2004-06-25 | 12707.3789 | 2004-07-25 | 12229.9268 | 2004-08-25 | 11573.2363 | 2004-09-25 |  | 2004-10-25 |  | 2004-11-25 | 10084.2236 | 2004-12-25 | 10275.0996
2004-01-26 | 9566.612 | 2004-02-26 | 11965.1898 | 2004-03-26 | 12388.5634 | 2004-04-26 | 12001.2441 | 2004-05-26 | 11208.5781 | 2004-06-26 | 12943.79 | 2004-07-26 | 12063.0488 | 2004-08-26 | 11701.4844 | 2004-09-26 |  | 2004-10-26 | 10558.0664 | 2004-11-26 | 10152.7314 | 2004-12-26
2004-01-27 |  | 2004-02-27 | 12342.08 | 2004-03-27 | 12432.746 | 2004-04-27 | 11899.2637 | 2004-05-27 | 11455.8018 | 2004-06-27 | 12945.3359 | 2004-07-27 | 12109.4053 | 2004-08-27 | 11390.9062 | 2004-09-27 |  | 2004-10-27 | 10522.5283 | 2004-11-27 | 10125.7305 | 2004-12-27 | 9877.8193
2004-01-28 | 10785.9771 | 2004-02-28 | 12560.2048 | 2004-03-28 | 12281.1103 | 2004-04-28 | 13413.5195 | 2004-05-28 | 11083.4189 | 2004-06-28 | 12962.333 | 2004-07-28 | 11639.6768 | 2004-08-28 | 11571.6895 | 2004-09-28 |  | 2004-10-28 | 8739.8535 | 2004-11-28 | 6492.356 | 2004-12-28 | 10020.0449
2004-01-29 | 11782.9256 | 2004-02-29 | 12414.8311 | 2004-03-29 | 12224.0683 | 2004-04-29 | 12897.4355 | 2004-05-29 | 11241.0254 | 2004-06-29 | 10839.2832 | 2004-07-29 | 11794.1934 | 2004-08-29 |  | 2004-09-29 |  | 2004-10-29 | 10099.2275 | 2004-11-29 | 9251.8418 | 2004-12-29 | 9883.5752
2004-01-30 | 11600.9194 |  |  | 2004-03-30 |  | 2004-04-30 | 13359.4395 | 2004-05-30 | 11275.0205 | 2004-06-30 | 12365.9004 | 2004-07-30 | 11951.7988 | 2004-08-30 |  | 2004-09-30 |  | 2004-10-30 | 9619.248 | 2004-11-30 | 9518.4746 | 2004-12-30 | 9811.3262
2004-01-31 | 11865.5274 |  |  | 2004-03-31 |  |  |  | 2004-05-31 | 10967.5332 |  |  | 2004-07-31 | 11970.3408 | 2004-08-31 |  |  |  | 2004-10-31 | 9740.6533 |  |  | 2004-12-31 | 9929.6543
Average | 9464.8334 |  | 11979.5229 |  | 12398.6252 |  | 12099.0009 |  | 11126.3946 |  | 12597.4686 |  | 12022.3775 |  | 11613.7452 |  | 11708.9513 |  | 10182.382 |  | 9683.5286 |  | 9734.7069
Date | FI-5091 | Date | FI-5091 | Date | FI-5091 | Date | FI-5091 | Date | FI-5091 | Date | FI-5091 | Date | FI-5091 | Date | FI-5091 | Date | FI-5091 | Date | FI-5091 | Date | FI-5091 | Date | FI-5091
| Kg/hr |  | Kg/hr |  | Kg/hr |  | Kg/hr |  | Kg/hr |  | Kg/hr |  | Kg/hr |  | Kg/hr |  | Kg/hr |  | Kg/hr |  | Kg/hr |  | Kg/hr
2005-01-01 | 10568.8828 | 2005-02-01 | 9738.3516 | 2005-03-01 | 9932.417 | 2005-04-01 | 9436.3125 | 2005-05-01 | 9238.9385 | 2005-06-01 | 9172.1719 | 2005-07-01 | 8989.6826 | 2005-08-01 | 10014.2178 | 2005-09-01 | 9738.3516 | 2005-10-01 | 10014.2178 | 2005-11-01 | 8989.6826 | 2005-12-01
2005-01-02 | 10830.0146 | 2005-02-02 | 11791.1758 | 2005-03-02 | 11380.5215 | 2005-04-02 | 11001.9717 | 2005-05-02 | 11740.1074 | 2005-06-02 |  | 2005-07-02 | 9354.2256 | 2005-08-02 | 10190.9131 | 2005-09-02 |  | 2005-10-02 | 10190.9131 | 2005-11-02 | 9354.2256 | 2005-12-02
2005-01-03 | 10830.0146 | 2005-02-03 | 9795.3223 | 2005-03-03 | 9917.2373 | 2005-04-03 | 9295.2568 | 2005-05-03 | 9307.499 | 2005-06-03 | 9330.7627 | 2005-07-03 | 9376.3623 | 2005-08-03 | 10139.0547 | 2005-09-03 |  | 2005-10-03 | 10139.0547 | 2005-11-03 | 9376.3623 | 2005-12-03
2005-01-04 | 9508.9033 | 2005-02-04 | 9954.9756 | 2005-03-04 |  | 2005-04-04 | 9080.4922 | 2005-05-04 | 9200.9863 | 2005-06-04 | 9200.1592 | 2005-07-04 | 9902.9561 | 2005-08-04 | 9760.4551 | 2005-09-04 |  | 2005-10-04 | 9760.4551 | 2005-11-04 | 9902.9561 | 2005-12-04
2005-01-05 | 10561.1562 | 2005-02-05 | 9812.8604 | 2005-03-05 | 9834.8223 | 2005-04-05 | 9179.5186 | 2005-05-05 | 8963.4883 | 2005-06-05 | 9134.248 | 2005-07-05 | 9713.918 | 2005-08-05 | 9827.3662 | 2005-09-05 |  | 2005-10-05 | 9827.3662 | 2005-11-05 | 9713.918 | 2005-12-05
2005-01-06 | 10003.3535 | 2005-02-06 | 9746.25 | 2005-03-06 | 9973.1602 | 2005-04-06 | 9209.0254 | 2005-05-06 | 9317.0557 | 2005-06-06 | 8942.5986 | 2005-07-06 | 9543.1074 | 2005-08-06 | 9238.9385 | 2005-09-06 |  | 2005-10-06 | 9143.0537 | 2005-11-06 | 9543.1074 | 2005-12-06 | 9200.9863
2005-01-07 | 10108.4258 | 2005-02-07 | 10181.2344 | 2005-03-07 |  | 2005-04-07 | 9026.4131 | 2005-05-07 | 9231.2314 | 2005-06-07 | 9120.0957 | 2005-07-07 | 10014.2178 | 2005-08-07 | 11740.1074 | 2005-09-07 | 9238.9385 | 2005-10-07 | 8481.4902 | 2005-11-07 | 10014.2178 | 2005-12-07 | 8963.4883
2005-01-08 | 9434.7354 | 2005-02-08 | 36.5896 | 2005-03-08 | 10069.8916 | 2005-04-08 | 8715.6055 | 2005-05-08 | 9348.0752 | 2005-06-08 | 9094.9111 | 2005-07-08 | 10190.9131 | 2005-08-08 | 9307.499 | 2005-09-08 | 11740.1074 | 2005-10-08 | 8717.5723 | 2005-11-08 | 10190.9131 | 2005-12-08 | 9317.0557
2005-01-09 | 10587.4238 | 2005-02-09 | 9619.5791 | 2005-03-09 | 9772.9785 | 2005-04-09 | 8829.1055 | 2005-05-09 | 9272.5625 | 2005-06-09 | 9160.6494 | 2005-07-09 | 10139.0547 | 2005-08-09 | 9200.9863 | 2005-09-09 | 9307.499 | 2005-10-09 | 9721.5264 | 2005-11-09 | 10139.0547 | 2005-12-09 | 9231.2314
2005-01-10 | 9502.7227 | 2005-02-10 | 9968.7734 | 2005-03-10 | 9428.1074 | 2005-04-10 | 8877.6143 | 2005-05-10 | 10341.8926 | 2005-06-10 | 8963.0049 | 2005-07-10 | 9760.4551 | 2005-08-10 | 8963.4883 | 2005-09-10 | 9200.9863 | 2005-10-10 | 9565.6377 | 2005-11-10 | 9760.4551 | 2005-12-10 | 9348.0752
2005-01-11 | 10726.4883 | 2005-02-11 | 9894.1162 | 2005-03-11 | 9626.2852 | 2005-04-11 | 8957.3379 | 2005-05-11 | 10010.9688 | 2005-06-11 | 8354.001 | 2005-07-11 | 9827.3662 | 2005-08-11 | 9317.0557 | 2005-09-11 | 8963.4883 | 2005-10-11 | 9238.9385 | 2005-11-11 | 9827.3662 | 2005-12-11 | 9272.5625
2005-01-12 | 9380.6553 | 2005-02-12 | 16.0508 | 2005-03-12 | 9918.6445 | 2005-04-12 | 9143.0537 | 2005-05-12 | 10580.6484 | 2005-06-12 | 8787.6064 | 2005-07-12 | 10568.8828 | 2005-08-12 | 9231.2314 | 2005-09-12 | 9317.0557 | 2005-10-12 | 11740.1074 | 2005-11-12 | 10568.8828 | 2005-12-12 | 10341.8926
2005-01-13 | 9518.1748 | 2005-02-13 | 27.5598 | 2005-03-13 | 9700.3477 | 2005-04-13 | 8481.4902 | 2005-05-13 | 9845.7041 | 2005-06-13 | 8847.8574 | 2005-07-13 | 10830.0146 | 2005-08-13 | 9348.0752 | 2005-09-13 | 9231.2314 | 2005-10-13 | 9307.499 | 2005-11-13 | 10830.0146 | 2005-12-13 | 10568.8828
2005-01-14 | 10633.7783 | 2005-02-14 | 10265.123 | 2005-03-14 | 14.8336 | 2005-04-14 | 8717.5723 | 2005-05-14 | 8971.4521 | 2005-06-14 | 9190.5078 | 2005-07-14 | 10830.0146 | 2005-08-14 | 9272.5625 | 2005-09-14 | 9348.0752 | 2005-10-14 | 9200.9863 | 2005-11-14 | 10830.0146 | 2005-12-14 | 10830.0146
2005-01-15 | 10677.042 | 2005-02-15 | 10061.8447 | 2005-03-15 | 9130.1846 | 2005-04-15 | 8830.9238 | 2005-05-15 | 8989.6826 | 2005-06-15 | 9052.0684 | 2005-07-15 | 9508.9033 | 2005-08-15 | 10341.8926 | 2005-09-15 | 9272.5625 | 2005-10-15 | 8963.4883 | 2005-11-15 | 9508.9033 | 2005-12-15 | 10830.0146
2005-01-16 |  | 2005-02-16 | 10323.2441 | 2005-03-16 | 9387.5674 | 2005-04-16 | 8608.5811 | 2005-05-16 | 9354.2256 | 2005-06-16 | 9084.3984 | 2005-07-16 | 9738.3516 | 2005-08-16 | 8989.6826 | 2005-09-16 | 10341.8926 | 2005-10-16 | 9317.0557 | 2005-11-16 |  | 2005-12-16 | 9508.9033
2005-01-17 | 9383.7451 | 2005-02-17 | 9831.7998 | 2005-03-17 | 9120.1621 | 2005-04-17 | 10232.4199 | 2005-05-17 | 9376.3623 | 2005-06-17 | 9120.1621 | 2005-07-17 | 9238.9385 | 2005-08-17 | 9354.2256 | 2005-09-17 |  | 2005-10-17 | 9231.2314 | 2005-11-17 |  | 2005-12-17 | 8786.876
2005-01-18 | 10.878 | 2005-02-18 | 10181.3896 | 2005-03-18 | 9251.6777 | 2005-04-18 |  | 2005-05-18 | 9902.9561 | 2005-06-18 | 9251.6777 | 2005-07-18 | 11740.1074 | 2005-08-18 | 9376.3623 | 2005-09-18 |  | 2005-10-18 | 9348.0752 | 2005-11-18 |  | 2005-12-18 | 10388.458
2005-01-19 |  | 2005-02-19 | 9882.3623 | 2005-03-19 | 9201.7256 | 2005-04-19 |  | 2005-05-19 | 9713.918 | 2005-06-19 | 9201.7256 | 2005-07-19 | 9307.499 | 2005-08-19 | 9902.9561 | 2005-09-19 |  | 2005-10-19 | 9272.5625 | 2005-11-19 | 10014.2178 | 2005-12-19 | 10220.3662
2005-01-20 |  | 2005-02-20 | 9985.2598 | 2005-03-20 | 9074.2314 | 2005-04-20 |  | 2005-05-20 | 9543.1074 | 2005-06-20 | 9074.2314 | 2005-07-20 | 9200.9863 | 2005-08-20 | 9713.918 | 2005-09-20 |  | 2005-10-20 | 10341.8926 | 2005-11-20 | 10190.9131 | 2005-12-20 | 10722.8535
2005-01-21 | 9627.3916 | 2005-02-21 | 10014.2178 | 2005-03-21 | 9420.5195 | 2005-04-21 |  | 2005-05-21 |  | 2005-06-21 | 9420.5195 | 2005-07-21 | 8963.4883 | 2005-08-21 | 9543.1074 | 2005-09-21 |  | 2005-10-21 | 8989.6826 | 2005-11-21 | 10139.0547 | 2005-12-21 | 10141.9385
2005-01-22 | 9609.6113 | 2005-02-22 | 10190.9131 | 2005-03-22 | 9538.4736 | 2005-04-22 |  | 2005-05-22 |  | 2005-06-22 | 9538.4736 | 2005-07-22 | 9317.0557 | 2005-08-22 | 10014.2178 | 2005-09-22 |  | 2005-10-22 | 9354.2256 | 2005-11-22 | 9760.4551 | 2005-12-22 | 10141.9385
2005-01-23 | 9565.4805 | 2005-02-23 | 10139.0547 | 2005-03-23 | 9543.6787 | 2005-04-23 |  | 2005-05-23 |  | 2005-06-23 | 9543.6787 | 2005-07-23 | 9231.2314 | 2005-08-23 | 10190.9131 | 2005-09-23 |  | 2005-10-23 | 9376.3623 | 2005-11-23 | 9827.3662 | 2005-12-23 | 10192.2754
2005-01-24 | 9695.2627 | 2005-02-24 | 9760.4551 | 2005-03-24 | 9359.2148 | 2005-04-24 |  | 2005-05-24 |  | 2005-06-24 | 9359.2148 | 2005-07-24 | 9348.0752 | 2005-08-24 | 10139.0547 | 2005-09-24 |  | 2005-10-24 | 9902.9561 | 2005-11-24 |  | 2005-12-24 | 7038.8911
2005-01-25 | 9367.042 | 2005-02-25 | 9827.3662 | 2005-03-25 | 9342.7314 | 2005-04-25 |  | 2005-05-25 |  | 2005-06-25 | 9342.7314 | 2005-07-25 | 9272.5625 | 2005-08-25 | 9760.4551 | 2005-09-25 |  | 2005-10-25 | 9713.918 | 2005-11-25 |  | 2005-12-25 | 7038.8911
2005-01-26 | 9865.0596 | 2005-02-26 | 9521.3301 | 2005-03-26 | 8546.5938 | 2005-04-26 |  | 2005-05-26 | 9166.0508 | 2005-06-26 | 8546.5938 | 2005-07-26 | 10341.8926 | 2005-08-26 | 9827.3662 | 2005-09-26 |  | 2005-10-26 | 9543.1074 | 2005-11-26 |  | 2005-12-26
2005-01-27 | 9753.6865 | 2005-02-27 | 10143.8799 | 2005-03-27 | 8824.8789 | 2005-04-27 |  | 2005-05-27 | 9245.5264 | 2005-06-27 | 8824.8789 | 2005-07-27 | 9143.0537 | 2005-08-27 |  | 2005-09-27 |  | 2005-10-27 | 10568.8828 | 2005-11-27 |  | 2005-12-27 | 9605.5215
2005-01-28 |  | 2005-02-28 | 10258.4619 | 2005-03-28 | 8983.4004 | 2005-04-28 |  | 2005-05-28 | 9241.9219 | 2005-06-28 | 8983.4004 | 2005-07-28 | 8481.4902 | 2005-08-28 |  | 2005-09-28 |  | 2005-10-28 | 10830.0146 | 2005-11-28 | 9143.0537 | 2005-12-28 | 9435.7412
2005-01-29 | 9746.7324 |  |  | 2005-03-29 | 9335.9131 | 2005-04-29 |  | 2005-05-29 | 9077.9131 | 2005-06-29 | 9335.9131 | 2005-07-29 | 8717.5723 | 2005-08-29 |  | 2005-09-29 |  | 2005-10-29 | 10830.0146 | 2005-11-29 | 8481.4902 | 2005-12-29 | 9435.7412
2005-01-30 | 9853.6816 |  |  | 2005-03-30 | 9721.5264 | 2005-04-30 |  | 2005-05-30 | 8972.2041 | 2005-06-30 | 9721.5264 | 2005-07-30 | 9721.5264 | 2005-08-30 |  | 2005-09-30 |  | 2005-10-30 | 9508.9033 | 2005-11-30 | 8717.5723 | 2005-12-30
2005-01-31 | 9787.4131 |  |  | 2005-03-31 | 9565.6377 |  |  | 2005-05-31 |  |  |  | 2005-07-31 | 9565.6377 | 2005-08-31 |  |  |  | 2005-10-31 |  |  |  | 2005-12-31 | 811.2068
| 9597.6947 |  | 8963.1979 |  | 9204.047 |  | 9154.2761 |  | 9518.1791 |  | 9127.5782 |  | 9673.5336 |  | 9719.4655 |  | 9609.108 |  | 9671.373 |  | 9774.9651 |  | 9223.9086
Date | FI-5091 | Date | FI-5091 | Date | FI-5091 | Date | FI-5091 | Date | FI-5091 | Date | FI-5091 | Date | FI-5091 | Date | FI-5091 | Date | FI-5091 | Date | FI-5091 | Date | FI-5091 | Date | FI-5091
| Kg/hr |  | Kg/hr |  | Kg/hr |  | Kg/hr |  | Kg/hr |  | Kg/hr |  | Kg/hr |  | Kg/hr |  | Kg/hr |  | Kg/hr |  | Kg/hr |  | Kg/hr
2006-01-01 | 11054.4219 | 2006-02-01 | 10228.916 | 2006-03-01 |  | 2006-04-01 | 10556.2881 | 2006-05-01 |  | 2006-06-01 | 11156.4873 | 2006-07-01 | 11229.8545 | 2006-08-01 | 9422.96 | 2006-09-01 |  | 2006-10-01 | 10934.0098 | 2006-11-01 | 11702.9795 | 2006-12-01 | 11086.7139
2006-01-02 | 10358.8125 | 2006-02-02 | 11791.1758 | 2006-03-02 |  | 2006-04-02 | 10416.6826 | 2006-05-02 |  | 2006-06-02 | 10801.5049 | 2006-07-02 | 11229.8311 | 2006-08-02 | 10090.5088 | 2006-09-02 |  | 2006-10-02 | 11035.667 | 2006-11-02 | 10385.8691 | 2006-12-02 | 9908.7334
2006-01-03 | 10076.3115 | 2006-02-03 | 10202.6885 | 2006-03-03 | 10234.7012 | 2006-04-03 | 10040.0928 | 2006-05-03 |  | 2006-06-03 | 10419.6084 | 2006-07-03 | 10338.6221 | 2006-08-03 | 9323.5938 | 2006-09-03 |  | 2006-10-03 | 10605.2793 | 2006-11-03 | 10457.8809 | 2006-12-03 | 10991.4629
2006-01-04 | 10257.5127 | 2006-02-04 | 10208.1963 | 2006-03-04 | 10010.5107 | 2006-04-04 | 10527.5117 | 2006-05-04 | 10426.9883 | 2006-06-04 | 10818.6924 | 2006-07-04 | 10638.7949 | 2006-08-04 | 9582.2871 | 2006-09-04 |  | 2006-10-04 | 10839.1191 | 2006-11-04 | 11174.1084 | 2006-12-04 | 11014.7686
2006-01-05 | 10191.7246 | 2006-02-05 | 10638.4229 | 2006-03-05 | 10279.7812 | 2006-04-05 | 10289.6436 | 2006-05-05 | 10356.6924 | 2006-06-05 | 10879.2734 | 2006-07-05 | 11194.9277 | 2006-08-05 | 8974.4814 | 2006-09-05 |  | 2006-10-05 | 10920.2695 | 2006-11-05 | 10690.9893 | 2006-12-05 | 11103.415
2006-01-06 | 9710.0605 | 2006-02-06 | 10574.0107 | 2006-03-06 | 10588.3232 | 2006-04-06 | 10520.2646 | 2006-05-06 | 10691.1309 | 2006-06-06 | 11095.5107 | 2006-07-06 | 11105.1094 | 2006-08-06 | 9946.0723 | 2006-09-06 |  | 2006-10-06 | 10442.0381 | 2006-11-06 | 11026.1885 | 2006-12-06 | 11192.0234
2006-01-07 | 10035.4551 | 2006-02-07 | 10091.4932 | 2006-03-07 | 9725.8975 | 2006-04-07 | 10225.2461 | 2006-05-07 | 10643.418 | 2006-06-07 | 10642.4902 | 2006-07-07 | 11032.8711 | 2006-08-07 | 9760.043 | 2006-09-07 |  | 2006-10-07 | 9849.4023 | 2006-11-07 | 11147.4121 | 2006-12-07 | 10827.1299
2006-01-08 | 9609.585 | 2006-02-08 | 10089.75 | 2006-03-08 | 9334.417 | 2006-04-08 | 9777.1641 | 2006-05-08 | 9913.4551 | 2006-06-08 | 11045.3115 | 2006-07-08 |  | 2006-08-08 | 8928.9375 | 2006-09-08 |  | 2006-10-08 | 11081.2197 | 2006-11-08 | 10376.0547 | 2006-12-08 | 11011.1475
2006-01-09 |  | 2006-02-09 | 10265.5508 | 2006-03-09 | 7953.2441 | 2006-04-09 | 10237.5996 | 2006-05-09 | 10740.0225 | 2006-06-09 | 10976.8525 | 2006-07-09 | 11077.6152 | 2006-08-09 |  | 2006-09-09 |  | 2006-10-09 | 11081.2197 | 2006-11-09 | 11059.7822 | 2006-12-09 | 11172.418
2006-01-10 | 10523.7393 | 2006-02-10 | 10231.6377 | 2006-03-10 | 10003.2646 | 2006-04-10 | 10662.7764 | 2006-05-10 | 10578.417 | 2006-06-10 | 10849.0957 | 2006-07-10 | 11094.3604 | 2006-08-10 | 9870.8691 | 2006-09-10 |  | 2006-10-10 | 11261.5645 | 2006-11-10 | 11084.4648 | 2006-12-10 | 11432.5527
2006-01-11 | 10149.3682 | 2006-02-11 | 9861 | 2006-03-11 | 10007.4121 | 2006-04-11 | 9902.2988 | 2006-05-11 | 10578.417 | 2006-06-11 | 10361.3701 | 2006-07-11 | 11065.5752 | 2006-08-11 | 9283.2305 | 2006-09-11 |  | 2006-10-11 | 10044.4502 | 2006-11-11 | 11302.7227 | 2006-12-11 | 11576.959
2006-01-12 | 9943.6562 | 2006-02-12 | 10394.8096 | 2006-03-12 | 10055.4941 | 2006-04-12 | 10328.1787 | 2006-05-12 | 9997.0264 | 2006-06-12 | 11023.6006 | 2006-07-12 | 11164.5576 | 2006-08-12 | 9192.1104 | 2006-09-12 |  | 2006-10-12 | 10094.3125 | 2006-11-12 | 11301.4521 | 2006-12-12
2006-01-13 | 10207.5742 | 2006-02-13 | 10235.751 | 2006-03-13 | 9984.7012 | 2006-04-13 | 10191.8818 | 2006-05-13 | 10267.2617 | 2006-06-13 | 11384.5967 | 2006-07-13 | 10991.0254 | 2006-08-13 |  | 2006-09-13 | 9512.8086 | 2006-10-13 | 10491.5713 | 2006-11-13 | 11607.5 | 2006-12-13 | 11576.959
2006-01-14 | 10225.873 | 2006-02-14 | 10235.751 | 2006-03-14 | 10389.4375 | 2006-04-14 | 10205.9883 | 2006-05-14 | 10779.8242 | 2006-06-14 | 10991.6602 | 2006-07-14 | 11483.9629 | 2006-08-14 | 9627.0117 | 2006-09-14 | 9948.0723 | 2006-10-14 | 11338.0586 | 2006-11-14 | 10636.5205 | 2006-12-14 | 11168.5488
2006-01-15 | 9883.0645 | 2006-02-15 | 10340.4961 | 2006-03-15 | 10256.4375 | 2006-04-15 | 10454.7988 | 2006-05-15 | 10839.2324 | 2006-06-15 | 10994.3203 | 2006-07-15 | 10983.5469 | 2006-08-15 | 9807.001 | 2006-09-15 | 10178.417 | 2006-10-15 | 10683.4902 | 2006-11-15 | 11067.4102 | 2006-12-15 | 11031.4248
2006-01-16 | 9966.5752 | 2006-02-16 | 10269.1924 | 2006-03-16 | 10053.1318 | 2006-04-16 |  | 2006-05-16 | 10592.1338 | 2006-06-16 | 10977.1963 | 2006-07-16 | 10981.582 | 2006-08-16 | 9718.7178 | 2006-09-16 | 10505.0273 | 2006-10-16 | 10592.1543 | 2006-11-16 | 11350.7988 | 2006-12-16 | 11419.8262
2006-01-17 | 9797.5303 | 2006-02-17 | 10604.6289 | 2006-03-17 | 10403.6191 | 2006-04-17 |  | 2006-05-17 | 10629.2471 | 2006-06-17 | 10971.4141 | 2006-07-17 | 10987.4248 | 2006-08-17 | 9634.4658 | 2006-09-17 | 10395.5791 | 2006-10-17 | 11095.9561 | 2006-11-17 | 11362.3633 | 2006-12-17 | 11561.4482
2006-01-18 | 9903.1143 | 2006-02-18 | 10382.3467 | 2006-03-18 | 10143.9707 | 2006-04-18 |  | 2006-05-18 | 11340.3857 | 2006-06-18 | 11078.8613 | 2006-07-18 | 11174.8008 | 2006-08-18 | 9728.8809 | 2006-09-18 | 10588.4248 | 2006-10-18 | 11078.3701 | 2006-11-18 | 11368.8555 | 2006-12-18
2006-01-19 | 10599.3623 | 2006-02-19 | 10263.0605 | 2006-03-19 | 9337.335 | 2006-04-19 |  | 2006-05-19 | 10792.1416 | 2006-06-19 | 11051.0527 | 2006-07-19 | 11404.998 | 2006-08-19 | 9535.1035 | 2006-09-19 | 9924.9414 | 2006-10-19 | 10722.6777 | 2006-11-19 | 11484.2852 | 2006-12-19
2006-01-20 | 10574.9111 | 2006-02-20 | 10454.7656 | 2006-03-20 | 10148.4111 | 2006-04-20 |  | 2006-05-20 | 11054.8838 | 2006-06-20 | 10917.8389 | 2006-07-20 | 11075.0801 | 2006-08-20 | 9808.1846 | 2006-09-20 | 10662.7881 | 2006-10-20 | 10768.6162 | 2006-11-20 | 10183.71 | 2006-12-20 | 11030.4209
2006-01-21 | 9883.5859 | 2006-02-21 | 10253.0947 | 2006-03-21 | 10278.8193 | 2006-04-21 |  | 2006-05-21 | 10879.2324 | 2006-06-21 | 10863.4756 | 2006-07-21 | 11069.4238 | 2006-08-21 | 9883.3105 | 2006-09-21 | 10419.8916 | 2006-10-21 | 10638.9707 | 2006-11-21 | 11155.5771 | 2006-12-21 | 11481.6641
2006-01-22 | 9894.9971 | 2006-02-22 | 10339.3975 | 2006-03-22 | 10427.9023 | 2006-04-22 |  | 2006-05-22 | 10879.2324 | 2006-06-22 | 10853.7197 | 2006-07-22 | 10934.8184 | 2006-08-22 | 9956.6729 | 2006-09-22 | 10981.3984 | 2006-10-22 | 10740.4609 | 2006-11-22 | 11316.0732 | 2006-12-22 | 11195.4814
2006-01-23 | 9893.8477 | 2006-02-23 | 10088.377 | 2006-03-23 | 10448.4297 | 2006-04-23 |  | 2006-05-23 | 11011.2783 | 2006-06-23 | 11124.6602 | 2006-07-23 | 10819.4219 | 2006-08-23 | 9956.6729 | 2006-09-23 | 10716.9678 | 2006-10-23 |  | 2006-11-23 | 10906.7451 | 2006-12-23 | 11360.8965
2006-01-24 |  | 2006-02-24 | 10294.9199 | 2006-03-24 | 10394.7666 | 2006-04-24 |  | 2006-05-24 | 11244.459 | 2006-06-24 | 11337.3408 | 2006-07-24 |  | 2006-08-24 | 9929.8125 | 2006-09-24 | 10788.2646 | 2006-10-24 | 10876.1992 | 2006-11-24 | 11084.6006 | 2006-12-24 | 11397.2783
2006-01-25 | 10339.4238 | 2006-02-25 | 9990.5664 | 2006-03-25 | 10453.7832 | 2006-04-25 |  | 2006-05-25 | 10952.2139 | 2006-06-25 | 10683.7656 | 2006-07-25 |  | 2006-08-25 | 9861.8311 | 2006-09-25 | 10528.8154 | 2006-10-25 | 10992.6572 | 2006-11-25 | 10819.9131 | 2006-12-25 | 11005.7549
2006-01-26 | 10313.1133 | 2006-02-26 | 10114.8682 | 2006-03-26 | 10682.4492 | 2006-04-26 |  | 2006-05-26 | 10637.7246 | 2006-06-26 | 11126.1035 | 2006-07-26 | 9664.6914 | 2006-08-26 | 9306.5508 | 2006-09-26 | 10948.3359 | 2006-10-26 | 10210.0508 | 2006-11-26 | 10976.4766 | 2006-12-26 | 10876.1094
2006-01-27 | 10134.9365 | 2006-02-27 | 10009.1328 | 2006-03-27 | 10153.4258 | 2006-04-27 |  | 2006-05-27 | 10571.3145 | 2006-06-27 | 10758.6279 | 2006-07-27 | 9693.6504 | 2006-08-27 | 8870.5801 | 2006-09-27 | 10665.1982 | 2006-10-27 | 11629.666 | 2006-11-27 | 11011.7939 | 2006-12-27 | 11451.1143
2006-01-28 | 10360.2412 | 2006-02-28 | 10379.1621 | 2006-03-28 | 9787.5 | 2006-04-28 |  | 2006-05-28 | 10832.0361 | 2006-06-28 | 11073.6611 | 2006-07-28 | 9561.9141 | 2006-08-28 | 9164.2666 | 2006-09-28 | 10891.3428 | 2006-10-28 | 10843.4951 | 2006-11-28 | 10703.1113 | 2006-12-28 | 10800.916
2006-01-29 | 10212.5039 |  |  | 2006-03-29 | 10410.7188 | 2006-04-29 |  | 2006-05-29 | 10752.0332 | 2006-06-29 | 11153.2959 | 2006-07-29 | 9724.0098 | 2006-08-29 | 8356.1377 | 2006-09-29 | 10889.1582 | 2006-10-29 | 11654.0322 | 2006-11-29 | 11467.8867 | 2006-12-29 | 10860.3359
2006-01-30 | 9808.3535 |  |  | 2006-03-30 | 10302.7617 | 2006-04-30 |  | 2006-05-30 | 10987.665 | 2006-06-30 | 11063.3457 | 2006-07-30 | 9590.1377 | 2006-08-30 | 9108.2871 | 2006-09-30 | 10491.458 | 2006-10-30 | 11158.4443 | 2006-11-30 | 11199.9688 | 2006-12-30 | 11581.6602
2006-01-31 | 10225.1309 |  |  | 2006-03-31 | 10502.4121 |  |  | 2006-05-31 | 11020.8828 |  |  | 2006-07-31 | 9553.5391 | 2006-08-31 |  |  |  | 2006-10-31 | 11110.6191 |  |  | 2006-12-31 | 10596.1162
| 10142.5788 |  | 10315.4701 |  | 10094.9331 |  | 10289.0944 |  | 10713.8839 |  | 10949.1578 |  | 10745.2195 |  | 9522.4493 |  | 10502.0494 |  | 10827.1347 |  | 11047.1165 |  | 11132.6171
Date | FI-5091 | Date | FI-5091 | Date | FI-5091 | Date | FI-5091 | Date | FI-5091 | Date | FI-5091 | Date | FI-5091 | Date | FI-5091 | Date | FI-5091 | Date | FI-5091 | Date | FI-5091 | Date | FI-5091
| Kg/hr |  | Kg/hr |  | Kg/hr |  | Kg/hr |  | Kg/hr |  | Kg/hr |  | Kg/hr |  | Kg/hr |  | Kg/hr |  | Kg/hr |  | Kg/hr |  | Kg/hr
2007-01-01 | 9505.6484 | 2007-02-01 | 11475.2754 | 2007-03-01 | 11882.6338 | 2007-04-01 | 11785.8379 | 2007-05-01 | 11575.8555 | 2007-06-01 |  | 2007-07-01 | 10991.4023 | 2007-08-01 | 10088.5186 | 2007-09-01 | 8921.6846 | 2007-10-01 | 9328.4619 | 2007-11-01 | 11730.7012 | 2007-12-01
2007-01-02 | 10075.4062 | 2007-02-02 | 11791.1758 | 2007-03-02 | 11380.5215 | 2007-04-02 | 11001.9717 | 2007-05-02 | 11740.1074 | 2007-06-02 |  | 2007-07-02 | 10262.4277 | 2007-08-02 | 9879.2402 | 2007-09-02 | 9002.1816 | 2007-10-02 | 8536.0469 | 2007-11-02 | 11664.7695 | 2007-12-02
2007-01-03 | 10436.4258 | 2007-02-03 | 11209.4082 | 2007-03-03 | 10917.7422 | 2007-04-03 | 11666.6162 | 2007-05-03 | 11547.2832 | 2007-06-03 |  | 2007-07-03 | 11173.0547 | 2007-08-03 | 9875.5498 | 2007-09-03 | 9128.5293 | 2007-10-03 | 8779.2461 | 2007-11-03 | 10965.3545 | 2007-12-03 | 10548.5781
2007-01-04 | 9790.79 | 2007-02-04 | 11224.708 | 2007-03-04 | 12069.7588 | 2007-04-04 | 11537.1582 | 2007-05-04 | 11427.7637 | 2007-06-04 |  | 2007-07-04 | 11251.2324 | 2007-08-04 | 10130.1338 | 2007-09-04 | 9466.7764 | 2007-10-04 | 10812.5605 | 2007-11-04 | 11866.5586 | 2007-12-04 | 10496.832
2007-01-05 | 9387.1943 | 2007-02-05 | 11700.9961 | 2007-03-05 | 12113.9355 | 2007-04-05 | 11157.1367 | 2007-05-05 |  | 2007-06-05 |  | 2007-07-05 | 11692.9404 | 2007-08-05 | 9883.8271 | 2007-09-05 | 9349.1699 | 2007-10-05 | 10900.6025 | 2007-11-05 | 11264.1885 | 2007-12-05
2007-01-06 | 9444.585 | 2007-02-06 | 11866.7344 | 2007-03-06 | 11173.6729 | 2007-04-06 | 11682.3125 | 2007-05-06 |  | 2007-06-06 |  | 2007-07-06 | 10973.0127 | 2007-08-06 | 10000.0586 | 2007-09-06 | 8871.9336 | 2007-10-06 | 11054.6211 | 2007-11-06 | 11592.7109 | 2007-12-06 | 9922.1836
2007-01-07 | 10468.6367 | 2007-02-07 | 11734.0283 | 2007-03-07 | 11114.9746 | 2007-04-07 | 11878.5693 | 2007-05-07 |  | 2007-06-07 |  | 2007-07-07 | 11101.0586 | 2007-08-07 | 9310.6094 | 2007-09-07 | 8951.8984 | 2007-10-07 | 11070.1963 | 2007-11-07 |  | 2007-12-07
2007-01-08 | 9589.0312 | 2007-02-08 | 11453.8525 | 2007-03-08 | 11244.4023 | 2007-04-08 | 11913.0811 | 2007-05-08 | 11930.0283 | 2007-06-08 |  | 2007-07-08 | 11238.5586 | 2007-08-08 | 8984.8418 | 2007-09-08 | 10673.1826 | 2007-10-08 | 11152.9043 | 2007-11-08 | 10872.2256 | 2007-12-08
2007-01-09 | 11301.8496 | 2007-02-09 | 11482.1523 | 2007-03-09 | 11182.624 | 2007-04-09 | 11763.5117 | 2007-05-09 | 11488.3037 | 2007-06-09 |  | 2007-07-09 | 10875.541 | 2007-08-09 | 9046.0713 | 2007-09-09 | 10558.3379 | 2007-10-09 | 10922.2393 | 2007-11-09 | 9774.1807 | 2007-12-09 | 10010.9443
2007-01-10 | 10953.4053 | 2007-02-10 | 11149.3145 | 2007-03-10 | 11272.7012 | 2007-04-10 | 12508.2373 | 2007-05-10 | 11267.6562 | 2007-06-10 |  | 2007-07-10 | 11036.665 | 2007-08-10 | 8823.2578 | 2007-09-10 | 10416.876 | 2007-10-10 | 11291.1816 | 2007-11-10 | 9860.5498 | 2007-12-10 | 10280.1455
2007-01-11 | 10068.5625 | 2007-02-11 | 11567.6846 | 2007-03-11 | 11230.7139 | 2007-04-11 | 11310.999 | 2007-05-11 | 11773.4766 | 2007-06-11 | 10651.6309 | 2007-07-11 | 11357.3936 | 2007-08-11 | 8939.085 | 2007-09-11 | 11272.9023 | 2007-10-11 | 9902.6914 | 2007-11-11 | 9987.1953 | 2007-12-11 | 10143.3047
2007-01-12 | 10751.5107 | 2007-02-12 | 11553.8584 | 2007-03-12 | 11245.1064 | 2007-04-12 | 11277.29 | 2007-05-12 | 11306.0635 | 2007-06-12 | 10698.8604 | 2007-07-12 | 11182.9453 | 2007-08-12 | 8461.9121 | 2007-09-12 | 11466.5664 | 2007-10-12 | 11057.5615 | 2007-11-12 | 10157.7256 | 2007-12-12 | 10516.1348
2007-01-13 | 10822.7998 | 2007-02-13 | 11402.9307 | 2007-03-13 | 11124.4707 | 2007-04-13 | 11912.5371 | 2007-05-13 | 11206.7295 | 2007-06-13 | 11097.6475 | 2007-07-13 | 11416.4082 | 2007-08-13 | 8624.5049 | 2007-09-13 | 11345.3369 | 2007-10-13 | 10772.5146 | 2007-11-13 | 9976.5518 | 2007-12-13 | 10777.6641
2007-01-14 | 9829.4502 | 2007-02-14 | 12024.0908 | 2007-03-14 | 11789.6016 | 2007-04-14 | 11487.9922 | 2007-05-14 | 11312.8818 | 2007-06-14 | 10753.1426 | 2007-07-14 | 11362.3857 | 2007-08-14 | 8721.9873 | 2007-09-14 | 9059.8984 | 2007-10-14 | 11250.7412 | 2007-11-14 | 9982.2998 | 2007-12-14 | 10986.2246
2007-01-15 | 9842.6963 | 2007-02-15 | 11524.6709 | 2007-03-15 | 11616.6094 | 2007-04-15 | 11737.9443 | 2007-05-15 | 11486.3643 | 2007-06-15 | 11149.6123 | 2007-07-15 | 11693.5635 | 2007-08-15 | 8687.4658 | 2007-09-15 | 8806.1465 | 2007-10-15 | 11334.5137 | 2007-11-15 | 8915.29 | 2007-12-15 | 10700.8467
2007-01-16 | 10329.7441 | 2007-02-16 | 11412.1182 | 2007-03-16 | 11590.9365 | 2007-04-16 | 11577.7852 | 2007-05-16 | 10995.3467 | 2007-06-16 | 11113.2021 | 2007-07-16 | 10761.5518 | 2007-08-16 | 8794.6387 | 2007-09-16 | 9005.6904 | 2007-10-16 | 11211.3643 | 2007-11-16 | 8463.0176 | 2007-12-16 | 10868.7432
2007-01-17 |  | 2007-02-17 | 11545.418 | 2007-03-17 | 11644.7432 | 2007-04-17 | 11644.3037 | 2007-05-17 | 11518.625 | 2007-06-17 |  | 2007-07-17 | 11190.8545 | 2007-08-17 | 8849.5 | 2007-09-17 | 8665.543 | 2007-10-17 | 11256.0811 | 2007-11-17 | 7956.8984 | 2007-12-17 | 10893.5664
2007-01-18 |  | 2007-02-18 | 11647.123 | 2007-03-18 | 11547.6602 | 2007-04-18 | 11423.4551 | 2007-05-18 | 11212.6162 | 2007-06-18 |  | 2007-07-18 | 11350.2803 | 2007-08-18 | 8990.2559 | 2007-09-18 | 8483.2715 | 2007-10-18 | 11258.4883 | 2007-11-18 | 8774.9932 | 2007-12-18 | 10905.79
2007-01-19 | 10716.1982 | 2007-02-19 | 11665.8174 | 2007-03-19 | 11874.8193 | 2007-04-19 | 11391.7568 | 2007-05-19 | 11342.6777 | 2007-06-19 |  | 2007-07-19 | 11250.1406 | 2007-08-19 | 8420.4268 | 2007-09-19 | 8755.9072 | 2007-10-19 | 11839.5908 | 2007-11-19 | 9343.2979 | 2007-12-19 | 10757.5166
2007-01-20 | 10171.7803 | 2007-02-20 | 11620.9385 | 2007-03-20 | 11702.7959 | 2007-04-20 | 11621.9131 | 2007-05-20 | 12109.8555 | 2007-06-20 |  | 2007-07-20 | 10918.4404 | 2007-08-20 | 8940.7734 | 2007-09-20 | 8753.3438 | 2007-10-20 | 11737.1846 | 2007-11-20 | 9341.9824 | 2007-12-20 | 9729.0107
2007-01-21 | 11053.2656 | 2007-02-21 | 12168.2783 | 2007-03-21 | 11869.335 | 2007-04-21 | 11508.1748 | 2007-05-21 | 11796.5938 | 2007-06-21 |  | 2007-07-21 | 11219.2148 | 2007-08-21 | 9042.2236 | 2007-09-21 | 8771.9639 | 2007-10-21 | 11511.3975 | 2007-11-21 | 9727.6855 | 2007-12-21 | 10182.1201
2007-01-22 |  | 2007-02-22 | 11430.999 | 2007-03-22 | 11612.8184 | 2007-04-22 |  | 2007-05-22 | 11268.9229 | 2007-06-22 |  | 2007-07-22 | 11334.9395 | 2007-08-22 | 8941.3408 | 2007-09-22 | 8491.9453 | 2007-10-22 | 11367.4092 | 2007-11-22 |  | 2007-12-22 | 7657.9678
2007-01-23 | 10500.8545 | 2007-02-23 | 11000.9434 | 2007-03-23 | 11536.7764 | 2007-04-23 | 11204.4141 | 2007-05-23 | 11178.6836 | 2007-06-23 | 10835.1777 | 2007-07-23 | 11227.291 | 2007-08-23 | 8981.0527 | 2007-09-23 | 8634.3857 | 2007-10-23 | 11883.1201 | 2007-11-23 |  | 2007-12-23 | 10444.1299
2007-01-24 | 10770.3018 | 2007-02-24 | 11042.4766 | 2007-03-24 | 11569.3193 | 2007-04-24 | 11257.75 | 2007-05-24 | 11324.7812 | 2007-06-24 | 10612.8906 | 2007-07-24 | 11308.0459 | 2007-08-24 | 9073.7197 | 2007-09-24 | 8616.0371 | 2007-10-24 | 11712.4082 | 2007-11-24 |  | 2007-12-24
2007-01-25 | 10869.4639 | 2007-02-25 | 10778.6631 | 2007-03-25 | 11680.6797 | 2007-04-25 | 12003.3262 | 2007-05-25 | 11105.3008 | 2007-06-25 | 10968.5342 | 2007-07-25 | 10995.6182 | 2007-08-25 | 8868.3271 | 2007-09-25 | 8696.9941 | 2007-10-25 | 9621.3955 | 2007-11-25 | 10906.7451 | 2007-12-25 | 7908.4263
2007-01-26 |  | 2007-02-26 | 11167.0664 | 2007-03-26 | 11527.5684 | 2007-04-26 | 11240.0879 | 2007-05-26 | 10955.3965 | 2007-06-26 | 10930.7129 | 2007-07-26 | 9948.1436 | 2007-08-26 | 9347.8311 | 2007-09-26 | 8433.0312 | 2007-10-26 |  | 2007-11-26 |  | 2007-12-26 | 8695.3379
2007-01-27 | 9983.2314 | 2007-02-27 | 10986.9834 | 2007-03-27 | 11533.4463 | 2007-04-27 | 11327.6416 | 2007-05-27 | 10911.5684 | 2007-06-27 | 11011.8594 | 2007-07-27 | 9857.7227 | 2007-08-27 | 9072.4121 | 2007-09-27 | 8580.8252 | 2007-10-27 | 10881.0713 | 2007-11-27 |  | 2007-12-27 | 8764.5947
2007-01-28 | 10653.2686 | 2007-02-28 | 11429.2773 | 2007-03-28 | 11726.8115 | 2007-04-28 | 11603.3145 | 2007-05-28 | 10904.0381 | 2007-06-28 | 11130.8398 | 2007-07-28 | 9805.2646 | 2007-08-28 | 9258.2178 | 2007-09-28 |  | 2007-10-28 | 11371.0283 | 2007-11-28 |  | 2007-12-28 | 9531.1182
2007-01-29 | 9419.6533 |  |  | 2007-03-29 | 11676.2051 | 2007-04-29 | 11558.1445 | 2007-05-29 |  | 2007-06-29 | 11239.8223 | 2007-07-29 | 9856.8535 | 2007-08-29 | 8894.4102 | 2007-09-29 | 8580.8252 | 2007-10-29 | 11814.8926 | 2007-11-29 |  | 2007-12-29 | 9215.3818
2007-01-30 | 9934.2617 |  |  | 2007-03-30 | 11796.625 | 2007-04-30 | 11668.3291 | 2007-05-30 |  | 2007-06-30 | 11115.9297 | 2007-07-30 |  | 2007-08-30 | 9260.8516 | 2007-09-30 | 10952.8203 | 2007-10-30 | 10877.4385 | 2007-11-30 |  | 2007-12-30 | 9270.1191
2007-01-31 | 10156.7129 |  |  | 2007-03-31 | 11785.8379 |  |  | 2007-05-31 |  |  |  | 2007-07-31 | 10367.8701 | 2007-08-31 | 8633.0654 |  |  | 2007-10-31 | 10975.5605 |  |  | 2007-12-31 | 11039.7227
| 10252.8418 |  | 11466.3208 |  | 11549.5434 |  | 11574.1928 |  | 11387.4768 |  | 10950.7045 |  | 10966.694 |  | 9123.4229 |  | 9334.9657 |  | 10916.1505 |  | 10148.8058 |  | 10009.8562

## Blower
History of Blower (K-503, K-504-315kW & K-504-400kW)
Date | K-503 | K-504-315 | Date | K-503 | K-504-315 | Date | K-503 | K-504-315 | Date | K-503 | K-504-315 | Date | K-503 | K-504-400 | Date | K-503 | K-504-400 | Date | K-503 | K-504-400 | Date | K-503 | K-504-400 | Date | K-503 | K-504-400 | Date | K-503 | K-504-400 | Date | K-503 | K-504-400 | Date | K-503 | K-504-400
| FC5044 | FC5043 |  | FC5044 | FC5043 |  | FC5044 | FC5043 |  | FC5044 | FC5043 |  | FC5044 | FC5043 |  | FC5044 | FC5043 |  | FC5044 | FC5043 |  | FC5044 | FC5043 |  | FC5044 | FC5043 |  | FC5044 | FC5043 |  | FC5044 | FC5043 |  | FC5044 | FC5043
| M3/Hr | M3/Hr |  | M3/Hr | M3/Hr |  | M3/Hr | M3/Hr |  | M3/Hr | M3/Hr |  | M3/Hr | M3/Hr |  | M3/Hr | M3/Hr |  | M3/Hr | M3/Hr |  | M3/Hr | M3/Hr |  | M3/Hr | M3/Hr |  | M3/Hr | M3/Hr |  | M3/Hr | M3/Hr |  | M3/Hr | M3/Hr
2004-01-01 | 7364.1469 | -4.2783 | 2004-02-01 | 5548.5018 | 1110.6053 | 2004-03-01 |  |  | 2004-04-01 | 8086.1358 | -2.6739 | 2004-05-01 | 7313.7548 | 4.5661 | 2004-06-01 | 8185.2754 | 14.9737 | 2004-07-01 | 8240.1922 | 17.3595 | 2004-08-01 | 7784.5217 | 17.9355 | 2004-09-01 | -34.6782 | 18.6346 | 2004-10-01 | -35.6654 | 6492.2163 | 2004-11-01 | 7891.724 | 33.1149 | 2004-12-01 | 7740.1766 | 33.444
2004-01-02 | -34.2257 | 6734.2638 | 2004-02-02 | 4871.5998 | 3079.3609 | 2004-03-02 |  |  | 2004-04-02 | 8130.6456 | -3.4555 | 2004-05-02 | 7362.008 | 3.8668 | 2004-06-02 | 8229.826 | 15.9198 | 2004-07-02 | 7924.3863 | 15.5496 | 2004-08-02 | 7807.9285 | 17.4829 | 2004-09-02 | -34.6782 | 19.622 | 2004-10-02 | -34.6782 | 6500.1147 | 2004-11-02 | 3753.8506 | 3139.1198 | 2004-12-02 | 7708.0078 | 36.2001
2004-01-03 | 0 | 0 | 2004-02-03 | 7986.9963 | -5.1421 | 2004-03-03 |  |  | 2004-04-03 | 8130.6456 | -3.4555 | 2004-05-03 | 7455.0178 | 3.7845 | 2004-06-03 | 8217.8069 | 15.4583 | 2004-07-03 | 7687.4394 | 17.9355 | 2004-08-03 | 7794.9295 | 19.3752 | 2004-09-03 | -35.6654 | 20.6093 | 2004-10-03 | -34.6782 | 26.5331 | 2004-11-03 | 2668.2421 | 4506.7181 | 2004-12-03 | 7794.23 | 36.7349
2004-01-04 | -33.8966 | 6167.9775 | 2004-02-04 | 8059.1553 | -5.0599 | 2004-03-04 | 8163.3904 | -5.7592 | 2004-04-04 | 8101.8912 | -4.1549 | 2004-05-04 | 7604.179 | 4.0725 | 2004-06-04 | 8178.4056 | 16.907 | 2004-07-04 | 7696.2016 | 15.8787 | 2004-08-04 | 7737.4616 | 18.6759 | 2004-09-04 | -35.6654 | 5911.6968 | 2004-10-04 | -34.6782 | 6149.6304 | 2004-11-04 | 8003.4922 | 35.5008 | 2004-12-04 | 7850.3816 | 38.3392
2004-01-05 | 7299.4393 | -4.1548 | 2004-02-05 | 8020.2762 | -4.5251 | 2004-03-05 | 8179.3923 | -4.3605 | 2004-04-05 | 8084.696 | -3.0853 | 2004-05-05 | 2515.6252 | 4337.77 | 2004-06-05 | 8211.7258 | 16.4134 | 2004-07-05 | 7743.303 | 17.9354 | 2004-08-05 | 7688.5913 | 17.6886 | 2004-09-05 | -35.6654 | 5993.6411 | 2004-10-05 | -34.6782 | 6165.4268 | 2004-11-05 | 7967.4563 | 32.6213 | 2004-12-05 | 7788.5942 | 38.7094
2004-01-06 | 6822.6663 | -3.6201 | 2004-02-06 | 8239.0405 | -4.3194 | 2004-03-06 | 8178.2406 | -5.0187 | 2004-04-06 | 3922.0853 | 3941.7481 | 2004-05-06 | 2515.6252 | 4337.77 | 2004-06-06 | 8226.0825 | 17.0716 | 2004-07-06 | 7759.2228 | 17.9767 | 2004-08-06 | 7712.9029 | 18.5113 | 2004-09-06 | -34.6782 | 6528.7456 | 2004-10-06 | -34.6782 | 6329.3149 | 2004-11-06 | 7971.5288 | 32.9092 | 2004-12-06 | 7945.8187 | 37.1874
2004-01-07 | 7060.1889 | -4.2783 | 2004-02-07 | 8179.5982 | -5.7592 | 2004-03-07 | 8161.6627 | -3.8669 | 2004-04-07 | -33.6498 | 7280.9689 | 2004-05-07 |  |  | 2004-06-07 | 8288.9802 | 16.7836 | 2004-07-07 | 7699.4925 | 17.6886 | 2004-08-07 | 7718.4975 | 17.9766 | 2004-09-07 | -34.6782 | 7679.9111 | 2004-10-07 |  |  | 2004-11-07 | 8050.1823 | 31.5928 | 2004-12-07 | 8174.7851 | 36.3235
2004-01-08 | -33.4441 | 6165.9207 | 2004-02-08 | 8255.9886 | -5.9649 | 2004-03-08 | 8254.6727 | -4.0726 | 2004-04-08 | -33.7732 | 7435.9715 | 2004-05-08 |  |  | 2004-06-08 | 8333.2432 | 16.9482 | 2004-07-08 | 7746.7996 | 18.0589 | 2004-08-08 | 7710.517 | 17.8532 | 2004-09-08 | 7957.3364 | 25.5458 | 2004-10-08 | 6680.7861 | 26.5331 | 2004-11-08 | 8009.4157 | 33.6497 | 2004-12-08 | 8185.7685 | 38.874
2004-01-09 | 7202.0691 | -4.484 | 2004-02-09 | 8202.1821 | -4.196 | 2004-03-09 | 8154.7927 | -3.2498 | 2004-04-09 | -33.6086 | 7685.794 | 2004-05-09 |  |  | 2004-06-09 | 8294.616 | 15.2205 | 2004-07-09 | 7608.6629 | 15.7964 | 2004-08-09 | 7684.3541 | 17.1539 | 2004-09-09 | 7946.4761 | 25.5458 | 2004-10-09 | 6680.7861 | 26.5331 | 2004-11-09 | 7986.9553 | 33.0737 | 2004-12-09 | 8108.6375 | 39.1208
2004-01-10 | -33.5675 | 6201.3805 | 2004-02-10 | 8258.8682 | -3.9492 | 2004-03-10 | 8198.3977 | -2.7151 | 2004-04-10 | 174.9127 | 7630.5888 | 2004-05-10 |  |  | 2004-06-10 | 8377.383 | 12.0941 | 2004-07-10 | 7667.2413 | 17.195 | 2004-08-10 | 3029.1743 | 3826.5658 | 2004-09-10 | 8115.3018 | 26.5331 | 2004-10-10 | 6894.0386 | 28.5075 | 2004-11-10 | 7844.7871 | 29.4949 | 2004-12-10 | 8139.8191 | 39.8202
2004-01-11 | 7182.8994 | -4.4428 | 2004-02-11 | 8242.0434 | -4.7308 | 2004-03-11 | 8032.8228 | -5.5124 | 2004-04-11 | 5120.1876 | 3535.6067 | 2004-05-11 |  |  | 2004-06-11 | 8384.335 | 14.2332 | 2004-07-11 | 7651.1981 | 17.4418 | 2004-08-11 | 0 | 0 | 2004-09-11 | 8020.5229 | 25.5458 | 2004-10-11 | 6841.7119 | 27.5202 | 2004-11-11 | 0 | 0 | 2004-12-11 | 8094.2809 | 40.067
2004-01-12 | -33.7321 | 6155.4309 | 2004-02-12 | 8159.2355 | -5.6358 | 2004-03-12 | 8032.8228 | -5.5124 | 2004-04-12 | 7874.8166 | 2.0568 | 2004-05-12 | 0 | 0 | 2004-06-12 | 8385.5691 | 14.3154 | 2004-07-12 | 7703.5238 | 14.8502 | 2004-08-12 | 0 | 0 | 2004-09-12 | 8031.3828 | 23.5711 | 2004-10-12 | 7107.2905 | 26.5331 | 2004-11-12 | 0 | 0 | 2004-12-12 | 7984.1581 | 37.5577
2004-01-13 | -33.403 | 6149.2605 | 2004-02-13 | 8120.3615 | -6.0471 | 2004-03-13 | 8105.4701 | -5.9237 | 2004-04-13 | 7854.3718 | 2.9206 | 2004-05-13 | 0 | 0 | 2004-06-13 | 8293.7929 | 14.8503 | 2004-07-13 | 7670.162 | 16.9893 | 2004-08-13 |  |  | 2004-09-13 | 8026.4468 | 23.5711 | 2004-10-13 | 6804.1958 | 27.5202 | 2004-11-13 | 0 | 0 | 2004-12-13 | 7853.22 | 36.7349
2004-01-14 | 7270.2323 | -4.0726 | 2004-02-14 | 8131.2625 | -6.0883 | 2004-03-14 | 8084.4902 | -4.484 | 2004-04-14 | 7806.818 | 3.332 | 2004-05-14 | -33.732 | 7.0343 | 2004-06-14 | 8289.803 | 15.7964 | 2004-07-14 | 7691.7999 | 15.3851 | 2004-08-14 |  |  | 2004-09-14 | 7993.8667 | 25.5458 | 2004-10-14 | 6898.9746 | 29.4949 | 2004-11-14 | 0 | 0 | 2004-12-14 | 7723.3517 | 35.5831
2004-01-15 | 7241.1488 | -4.813 | 2004-02-15 | 8194.3663 | -5.6769 | 2004-03-15 | 8092.9646 | -4.7308 | 2004-04-15 | 7789.0469 | 2.3035 | 2004-05-15 | -33.9377 | 5.8002 | 2004-06-15 | 8187.2493 | 15.6318 | 2004-07-15 | 7572.0102 | 16.3723 | 2004-08-15 |  |  | 2004-09-15 | 7990.9053 | 23.5711 | 2004-10-15 | 6849.6108 | 29.4949 | 2004-11-15 |  |  | 2004-12-15 | 5643.6098 | 1919.8852
2004-01-16 | 7277.8014 | -3.8669 | 2004-02-16 | 8194.3663 | -5.6769 | 2004-03-16 | 8162.1973 | -4.3194 | 2004-04-16 | 7751.3657 | 2.3036 | 2004-05-16 | -34.3902 | 4.8129 | 2004-06-16 | 8124.7628 | 14.8091 | 2004-07-16 | 7583.6519 | 17.6064 | 2004-08-16 | 0 | 0 | 2004-09-16 | 7911.9219 | 23.5711 | 2004-10-16 | 6800.2466 | 27.5202 | 2004-11-16 |  |  | 2004-12-16 | 8038.4995 | 38.0924
2004-01-17 | -32.6625 | 6142.9254 | 2004-02-17 | 8099.2585 | -6.2528 | 2004-03-17 | 8146.7302 | -5.7592 | 2004-04-17 | 7735.2813 | 1.9745 | 2004-05-17 | -34.5137 | 5.2654 | 2004-06-17 | 8177.6236 | 15.3439 | 2004-07-17 | 7620.0167 | 17.1539 | 2004-08-17 | 7450.8628 | 16.6602 | 2004-09-17 | 7943.5151 | 25.5458 | 2004-10-17 | -33.6909 | 6978.9443 | 2004-11-17 | 8137.3653 | 35.7619 | 2004-12-17 | 7995.1002 | 36.6937
2004-01-18 | -30.3177 | 306.4673 | 2004-02-18 | 8025.7471 | -5.4712 | 2004-03-18 | 8113.4506 | -6.1294 | 2004-04-18 | 7706.1151 | -1.0697 | 2004-05-18 | -34.6782 | 1.8509 | 2004-06-18 | 8305.2706 | 18.4702 | 2004-07-18 | 7606.4416 | 17.6064 | 2004-08-18 | 7317.5806 | 14.6855 | 2004-09-18 | 8093.5825 | 25.5458 | 2004-10-18 | 6968.084 | 28.5075 | 2004-11-18 | 8087.3287 | 30.8523 | 2004-12-18 | 7995.1002 | 36.6937
2004-01-19 | -33.403 | 6262.8386 | 2004-02-19 | 8026.7344 | -7.1167 | 2004-03-19 | 8164.7479 | -3.1676 | 2004-04-19 | 6796.5034 | 974.978 | 2004-05-19 | -34.0611 | 6501.1017 | 2004-06-19 | 8276.9578 | 16.1022 | 2004-07-19 | 7709.6531 | 16.5368 | 2004-08-19 |  |  | 2004-09-19 | 7159.6157 | 24.5584 | 2004-10-19 | 7027.3208 | 27.5202 | 2004-11-19 | 8054.3371 | 32.0041 | 2004-12-19 | 7986.6674 | 38.9974
2004-01-20 | -32.498 | -4.5662 | 2004-02-20 | 8065.9376 | -5.7592 | 2004-03-20 | 8135.6643 | -3.2087 | 2004-04-20 | 7209.5561 | 656.6632 | 2004-05-20 | -33.732 | 6184.1444 | 2004-06-20 | 8254.0141 | 15.2616 | 2004-07-20 | 7767.5734 | 17.195 | 2004-08-20 | 7804.3086 | 15.6729 | 2004-09-20 | 7268.2158 | 25.5458 | 2004-10-20 | 6906.8726 | 28.5075 | 2004-11-20 | 8005.3022 | 31.346 | 2004-12-20 | 8100.9038 | 36.1178
2004-01-21 | -34.206 | 6217.2377 | 2004-02-21 | 8155.41 | -4.6485 | 2004-03-21 | 8207.6945 | -2.7151 | 2004-04-21 | 7830.5946 | -0.041179 | 2004-05-21 | -33.732 | 6184.1444 | 2004-06-21 | 8312.1136 | 17.0036 | 2004-07-21 | 7781.2309 | 17.8532 | 2004-08-21 | 7935.6162 | 16.6602 | 2004-09-21 | 7151.7178 | 25.5458 | 2004-10-21 | 7143.8196 | 32.9091 | 2004-11-21 | 8001.9292 | 29.0423 | 2004-12-21 | 8011.1024 | 37.2285
2004-01-22 | -32.0866 | -3.7023 | 2004-02-22 | 8124.8865 | -4.9776 | 2004-03-22 | 8188.8949 | -4.3605 | 2004-04-22 | 7727.3832 | 1.7277 | 2004-05-22 | -33.7732 | 6519.2428 | 2004-06-22 | 8212.2194 | 16.8659 | 2004-07-22 | 7705.9508 | 18.0589 | 2004-08-22 | 7766.7915 | 16.6602 | 2004-09-22 | 7001.6514 | 25.5458 | 2004-10-22 | 7247.7718 | 35.2951 | 2004-11-22 | 7848.2425 | 28.8778 | 2004-12-22 | 8049.1539 | 36.488
2004-01-23 | -34.3491 | 6196.115 | 2004-02-23 | 8034.5916 | -3.908 | 2004-03-23 | 8222.2568 | -2.5505 | 2004-04-23 | 7777.652 | 1.7688 | 2004-05-23 | -34.1434 | 7344.196 | 2004-06-23 | 0 | 0 | 2004-07-23 | 7689.8664 | 17.6886 | 2004-08-23 | 7726.3135 | 17.6476 | 2004-09-23 | 7143.8198 | 25.5458 | 2004-10-23 | 7204.8251 | 33.8553 | 2004-11-23 | 7930.3512 | 29.0835 | 2004-12-23 | 8066.1845 | 34.8014
2004-01-24 | -34.3491 | 6196.0327 | 2004-02-24 | 8052.3215 | -5.4712 | 2004-03-24 | 8216.7855 | -3.3732 | 2004-04-24 | 7778.5158 | 0.74038 | 2004-05-24 | -34.5923 | 7362.9095 | 2004-06-24 | 8248.6252 | 16.0432 | 2004-07-24 | 7670.4911 | 17.4418 | 2004-08-24 | 0 | 0 | 2004-09-24 | 7133.9468 | 26.5331 | 2004-10-24 | 7219.5932 | 34.5958 | 2004-11-24 | 8007.1944 | 29.7417 | 2004-12-24 | 8010.362 | 37.2285
2004-01-25 | -34.1023 | 6226.1036 | 2004-02-25 | 7970.953 | -4.5251 | 2004-03-25 | 8211.0677 | -2.7973 | 2004-04-25 | 7751.2423 | 1.7276 | 2004-05-25 | -34.1434 | 7416.4729 | 2004-06-25 | 8245.8278 | 14.9737 | 2004-07-25 | 7726.5603 | 18.0178 | 2004-08-25 | 7738.1611 | 17.6476 | 2004-09-25 | -35.6654 | 6005.4883 | 2004-10-25 | 7239.8002 | 33.8303 | 2004-11-25 | 6772.4805 | 1376.1421 | 2004-12-25 | 7979.3861 | 34.3078
2004-01-26 | -34.5923 | 6187.7911 | 2004-02-26 | 7970.953 | -4.5251 | 2004-03-26 | 8157.7135 | -2.7562 | 2004-04-26 | 7894.1509 | 1.8099 | 2004-05-26 | -34.8839 | 7411.0017 | 2004-06-26 | 7894.1509 | 1.8099 | 2004-07-26 | 7685.9174 | 17.9355 | 2004-08-26 | 7578.2217 | 17.6476 | 2004-09-26 | -33.6909 | 6006.4756 | 2004-10-26 | 7247.8953 | 33.6908 | 2004-11-26 | 5285.6396 | 3608.9535 | 2004-12-26
2004-01-27 |  |  | 2004-02-27 | 8154.6282 | -4.4017 | 2004-03-27 | 8111.5241 | -2.8707 | 2004-04-27 | 6321.1294 | 3239.5056 | 2004-05-27 | 4331.8465 | 4419.0558 | 2004-06-27 | 8342.6639 | 17.5241 | 2004-07-27 | 7667.7761 | 17.7709 | 2004-08-27 | 7491.3413 | 18.6346 | 2004-09-27 | -34.6782 | 27.5202 | 2004-10-27 | 7274.7985 | 33.7319 | 2004-11-27 | 5608.8174 | 1698.4667 | 2004-12-27 | 7982.3891 | 35.1717
2004-01-28 | 4769.1282 | 2646.8097 | 2004-02-28 | 8226.4527 | -3.6201 | 2004-03-28 | 8066.9663 | -4.6485 | 2004-04-28 | 4767.6884 | 4693.4368 | 2004-05-28 | 7432.2693 | 16.9482 | 2004-06-28 | 8342.6639 | 17.5241 | 2004-07-28 | 7652.5556 | 17.5652 | 2004-08-28 | 7513.062 | 17.6476 | 2004-09-28 | -35.6654 | 27.5202 | 2004-10-28 | 7460.8592 | 33.5674 | 2004-11-28 | -33.4441 | 6570.787 | 2004-12-28 | 8036.9632 | 35.9336
2004-01-29 | 7837.9994 | -2.4683 | 2004-02-29 | 8175.1143 | -3.8669 | 2004-03-29 | 8090.6197 | -2.5094 | 2004-04-29 | 4676.1186 | 4634.6527 | 2004-05-29 | 7483.4431 | 18.0178 | 2004-06-29 | 4840.5006 | 3520.2629 | 2004-07-29 | 7659.3842 | 17.6475 | 2004-08-29 | -34.6782 | 5985.7427 | 2004-09-29 | -34.6782 | 27.5202 | 2004-10-29 | 7935.9868 | 33.7319 | 2004-11-29 | 2909.7961 | 5048.3224 | 2004-12-29 | 8121.4722 | 36.2413
2004-01-30 | 7780.2437 | -3.9903 |  |  |  | 2004-03-30 |  |  | 2004-04-30 | 5846.8654 | 2810.9448 | 2004-05-30 | 7481.2628 | 17.1128 | 2004-06-30 | 8274.2124 | 16.7425 | 2004-07-30 | 7692.2935 | 18.0177 | 2004-08-30 | -34.6782 | 6016.3486 | 2004-09-30 | -34.6782 | 28.5075 | 2004-10-30 | 7932.6136 | 33.6908 | 2004-11-30 | 7810.2323 | 35.6242 | 2004-12-30 | 8100.1634 | 37.4342
2004-01-31 | 7866.5483 | -4.1137 |  |  |  | 2004-03-31 | [5 empty] | 2004-05-31 | 7636.1833 | 16.4545 |  |  |  | 2004-07-31 | 7735.487 | 18.388 | 2004-08-31 | -34.6782 | 18.6346 |  |  |  | 2004-10-31 | 7893.3693 | 33.2383 |  |  |  | 2004-12-31 | 8015.8745 | 35.0483
K-503 ratio = |  |  | K-503 ratio = |  |  | K-503 ratio = |  |  | K-503 ratio = |  |  | K-503 ratio = |  | 0 | K-503 ratio = |  | 0.0013551 | K-503 ratio = |  | 0.2139 | K-503 ratio = |  | 0.98373 | K-503 ratio = |  | 0.14062 | K-503 ratio = |  | -0.0009064 | K-503 ratio = |  |  | K-503 ratio =
Normal Running |  |  | Normal Running |  |  | Normal Running |  |  | Normal Running |  |  | Normal Running |  |  | Normal Running |  |  | Normal Running |  |  | Normal Running |  |  | Normal Running |  |  | Normal Running |  |  | Normal Running |  |  | Normal Running
Date | K-503 | K-504-315 | Date | K-503 | K-504-315 | Date | K-503 | K-504-315 | Date | K-503 | K-504-315 | Date | K-503 | K-504-400 | Date | K-503 | K-504-400 | Date | K-503 | K-504-400 | Date | K-503 | K-504-400 | Date | K-503 | K-504-400 | Date | K-503 | K-504-400 | Date | K-503 | K-504-400 | Date | K-503 | K-504-400
| FC5044 | FC5043 |  | FC5044 | FC5043 |  | FC5044 | FC5043 |  | FC5044 | FC5043 |  | FC5044 | FC5043 |  | FC5044 | FC5043 |  | FC5044 | FC5043 |  | FC5044 | FC5043 |  | FC5044 | FC5043 |  | FC5044 | FC5043 |  | FC5044 | FC5043 |  | FC5044 | FC5043
| M3/Hr | M3/Hr |  | M3/Hr | M3/Hr |  | M3/Hr | M3/Hr |  | M3/Hr | M3/Hr |  | M3/Hr | M3/Hr |  | M3/Hr | M3/Hr |  | M3/Hr | M3/Hr |  | M3/Hr | M3/Hr |  | M3/Hr | M3/Hr |  | M3/Hr | M3/Hr |  | M3/Hr | M3/Hr |  | M3/Hr | M3/Hr
2005-01-01 | 7364.1469 | -4.2783 | 2005-02-01 | 8000.7773 | 33.444 | 2005-03-01 | 8178.8576 | 42.2061 | 2005-04-01 | 7652.4323 | 41.7124 | 2005-05-01 | 5164.3274 | 2998.1966 | 2005-06-01 | 2171.4766 | 5349.4421 | 2005-07-01 | 7456.1696 | 48.0886 | 2005-08-01 | 8099.5054 | 36.4057 | 2005-09-01 | 8000.7773 | 33.444 | 2005-10-01 | 8099.5054 | 36.4057 | 2005-11-01 | 7456.1696 | 48.0886 | 2005-12-01
2005-01-02 | -34.2257 | 6734.2638 | 2005-02-02 | 8081.7334 | 32.4566 | 2005-03-02 | 8220.1176 | 40.9308 | 2005-04-02 | 7538.6485 | 41.1365 | 2005-05-02 | 7642.2714 | 49.0347 | 2005-06-02 | 7532.1899 | 49.8163 | 2005-07-02 | 7776.0067 | 48.0886 | 2005-08-02 | 7874.8986 | 35.5009 | 2005-09-02 |  |  | 2005-10-02 | 7874.8986 | 35.5009 | 2005-11-02 | 7776.0067 | 48.0886 | 2005-12-02
2005-01-03 | 0 | 0 | 2005-02-03 | 8106.4165 | 34.4313 | 2005-03-03 | 7809.7801 | 42.9876 | 2005-04-03 | 7702.6189 | 41.301 | 2005-05-03 | 7540.8698 | 47.019 | 2005-06-03 | 7553.2519 | 49.1992 | 2005-07-03 | 7810.2732 | 49.0347 | 2005-08-03 | 8202.3466 | 39.4499 | 2005-09-03 |  |  | 2005-10-03 | 8202.3466 | 39.4499 | 2005-11-03 | 7810.2732 | 49.0347 | 2005-12-03
2005-01-04 | -33.8966 | 6167.9775 | 2005-02-04 | 8018.5488 | 34.4313 | 2005-03-04 | 3390.7648 | 3757.5797 | 2005-04-04 | 7674.3581 | 40.8486 | 2005-05-04 | 7548.9737 | 49.0759 | 2005-06-04 | 7573.7791 | 50.2689 | 2005-07-04 | 7806.0774 | 48.3765 | 2005-08-04 | 8217.4849 | 41.7125 | 2005-09-04 |  |  | 2005-10-04 | 8217.4849 | 41.7125 | 2005-11-04 | 7806.0774 | 48.3765 | 2005-12-04
2005-01-05 | 7299.4393 | -4.1548 | 2005-02-05 | 8013.6128 | 33.444 | 2005-03-05 | 7989.3823 | 40.4372 | 2005-04-05 | 7579.7439 | 39.6968 | 2005-05-05 | 7553.9102 | 48.829 | 2005-06-05 | 7504.5463 | 49.3227 | 2005-07-05 | 0 | 0 | 2005-08-05 | 8196.5052 | 40.067 | 2005-09-05 |  |  | 2005-10-05 | 8196.5052 | 40.067 | 2005-11-05 | 0 | 0 | 2005-12-05
2005-01-06 | 6822.6663 | -3.6201 | 2005-02-06 | 7998.8027 | 35.4187 | 2005-03-06 | 7988.8475 | 36.9817 | 2005-04-06 | 7554.1982 | 42.9465 | 2005-05-06 | 7511.992 | 47.1425 | 2005-06-06 | 7528.4877 | 49.0759 | 2005-07-06 | 7922.3105 | 51.773 | 2005-08-06 | 2171.4766 | 5349.4421 | 2005-09-06 |  |  | 2005-10-06 | 7433.2567 | 40.067 | 2005-11-06 | 7922.3105 | 51.773 | 2005-12-06 | 7573.7791 | 50.2689
2005-01-07 | 7060.1889 | -4.2783 | 2005-02-07 | 8132.0859 | 34.4313 | 2005-03-07 | 0 | 0 | 2005-04-07 | 7441.9774 | 39.9686 | 2005-05-07 | 7495.7429 | 46.6488 | 2005-06-07 | 7521.8648 | 48.3766 | 2005-07-07 | 8099.5054 | 36.4057 | 2005-08-07 | 7532.1899 | 49.8163 | 2005-09-07 | 2171.4766 | 5349.4421 | 2005-10-07 | 7451.6857 | 40.2727 | 2005-11-07 | 8099.5054 | 36.4057 | 2005-12-07 | 7504.5463 | 49.3227
2005-01-08 | -33.4441 | 6165.9207 | 2005-02-08 | -29.7418 | 6196.0322 | 2005-03-08 | 8038.2937 | 41.8769 | 2005-04-08 | 7344.1546 | 39.9024 | 2005-05-08 | 7607.2231 | 48.3354 | 2005-06-08 | 7546.7113 | 48.2943 | 2005-07-08 | 7874.8986 | 35.5009 | 2005-08-08 | 7553.2519 | 49.1992 | 2005-09-08 | 7532.1899 | 49.8163 | 2005-10-08 | 7512.7325 | 42.6586 | 2005-11-08 | 7874.8986 | 35.5009 | 2005-12-08 | 7528.4877 | 49.0759
2005-01-09 | 7202.0691 | -4.484 | 2005-02-09 | 8031.3828 | 37.393 | 2005-03-09 | 8059.1502 | 42.1649 | 2005-04-09 | 7330.6209 | 42.494 | 2005-05-09 | 7633.9621 | 2487.0765 | 2005-06-09 | 7488.6673 | 47.8006 | 2005-07-09 | 8202.3466 | 39.4499 | 2005-08-09 | 7573.7791 | 50.2689 | 2005-09-09 | 7553.2519 | 49.1992 | 2005-10-09 | 7785.9205 | 41.301 | 2005-11-09 | 8202.3466 | 39.4499 | 2005-12-09 | 7521.8648 | 48.3766
2005-01-10 | -33.5675 | 6201.3805 | 2005-02-10 | 8119.2515 | 35.4187 | 2005-03-10 | 7998.4324 | 41.8358 | 2005-04-10 | 7370.7701 | 41.8769 | 2005-05-10 | 5113.6059 | 4524.7859 | 2005-06-10 | 7460.9001 | 48.3354 | 2005-07-10 | 8217.4849 | 41.7125 | 2005-08-10 | 7504.5463 | 49.3227 | 2005-09-10 | 7573.7791 | 50.2689 | 2005-10-10 | 7771.5227 | 41.5479 | 2005-11-10 | 8217.4849 | 41.7125 | 2005-12-10 | 7546.7113 | 48.2943
2005-01-11 | 7182.8994 | -4.4428 | 2005-02-11 | 7998.8027 | 36.4057 | 2005-03-11 | 7912.4156 | 43.8927 | 2005-04-11 | 7433.2567 | 40.067 | 2005-05-11 | 7622.9374 | 5465.8996 | 2005-06-11 | 7399.0523 | 48.1673 | 2005-07-11 | 8196.5052 | 40.067 | 2005-08-11 | 7528.4877 | 49.0759 | 2005-09-11 | 7504.5463 | 49.3227 | 2005-10-11 | 2171.4766 | 5349.4421 | 2005-11-11 | 8196.5052 | 40.067 | 2005-12-11 | 7488.6673 | 47.8006
2005-01-12 | -33.7321 | 6155.4309 | 2005-02-12 | -29.7418 | 6042.0171 | 2005-03-12 | 7918.7095 | 44.1395 | 2005-04-12 | 7433.2567 | 40.067 | 2005-05-12 | 7812.6593 | 2498.8003 | 2005-06-12 | 7330.8265 | 47.8006 | 2005-07-12 | 7364.1469 | -4.2783 | 2005-08-12 | 7521.8648 | 48.3766 | 2005-09-12 | 7528.4877 | 49.0759 | 2005-10-12 | 7532.1899 | 49.8163 | 2005-11-12 | 7364.1469 | -4.2783 | 2005-12-12 | 7460.9001 | 48.3354
2005-01-13 | -33.403 | 6149.2605 | 2005-02-13 | -28.7546 | 6650.1807 | 2005-03-13 | 6557.1708 | 482.4909 | 2005-04-13 | 7451.6857 | 40.2727 | 2005-05-13 | 7689.4141 | 48.7879 | 2005-06-13 | 7432.5572 | 47.4304 | 2005-07-13 | -34.2257 | 6734.2638 | 2005-08-13 | 7546.7113 | 48.2943 | 2005-09-13 | 7521.8648 | 48.3766 | 2005-10-13 | 7553.2519 | 49.1992 | 2005-11-13 | -34.2257 | 6734.2638 | 2005-12-13 | 7364.1469 | -4.2783
2005-01-14 | 7270.2323 | -4.0726 | 2005-02-14 | 8143.9331 | 35.4187 | 2005-03-14 | 3258.3873 | 3365.4247 | 2005-04-14 | 7512.7325 | 42.6586 | 2005-05-14 | 7456.1696 | 48.0886 | 2005-06-14 | 7425.7697 | 46.0729 | 2005-07-14 | 0 | 0 | 2005-08-14 | 7488.6673 | 47.8006 | 2005-09-14 | 7546.7113 | 48.2943 | 2005-10-14 | 7573.7791 | 50.2689 | 2005-11-14 | 0 | 0 | 2005-12-14 | -34.2257 | 6734.2638
2005-01-15 | 7241.1488 | -4.813 | 2005-02-15 | 8198.2334 | 34.4313 | 2005-03-15 | 7709.8177 | 42.6174 | 2005-04-15 | 7455.7172 | 39.2853 | 2005-05-15 | 7456.1696 | 48.0886 | 2005-06-15 | 7512.9381 | 45.3324 | 2005-07-15 | -33.8966 | 6167.9775 | 2005-08-15 | 7460.9001 | 48.3354 | 2005-09-15 | 7488.6673 | 47.8006 | 2005-10-15 | 7504.5463 | 49.3227 | 2005-11-15 | -33.8966 | 6167.9775 | 2005-12-15 | 0 | 0
2005-01-16 | 7277.8014 | -3.8669 | 2005-02-16 | 8099.5054 | 36.4057 | 2005-03-16 | 7465.4665 | 44.1806 | 2005-04-16 | -27.1914 | 6302.4532 | 2005-05-16 | 7776.0067 | 48.0886 | 2005-06-16 | 7511.9097 | 46.4431 | 2005-07-16 | 8000.7773 | 33.444 | 2005-08-16 | 7456.1696 | 48.0886 | 2005-09-16 | 7460.9001 | 48.3354 | 2005-10-16 | 7528.4877 | 49.0759 | 2005-11-16 |  |  | 2005-12-16 | -20.3627 | -20.3627
2005-01-17 | -32.6625 | 6142.9254 | 2005-02-17 | 7874.8986 | 35.5009 | 2005-03-17 | 7725.0382 | 40.9308 | 2005-04-17 | 2762.239 | 3760.5005 | 2005-05-17 | 7810.2732 | 49.0347 | 2005-06-17 | 7725.0382 | 40.9308 | 2005-07-17 | 2171.4766 | 5349.4421 | 2005-08-17 | 7776.0067 | 48.0886 | 2005-09-17 |  |  | 2005-10-17 | 7521.8648 | 48.3766 | 2005-11-17 |  |  | 2005-12-17 | 4461.7972 | 3466.8263
2005-01-18 | -30.3177 | 306.4673 | 2005-02-18 | 8202.3466 | 39.4499 | 2005-03-18 | 7682.9966 | 40.7251 | 2005-04-18 | -27.1914 | 6302.4532 | 2005-05-18 | 7806.0774 | 48.3765 | 2005-06-18 | 7682.9966 | 40.7251 | 2005-07-18 | 7532.1899 | 49.8163 | 2005-08-18 | 7810.2732 | 49.0347 | 2005-09-18 |  |  | 2005-10-18 | 7546.7113 | 48.2943 | 2005-11-18 |  |  | 2005-12-18 | 4461.7972 | 3466.8263
2005-01-19 | -30.3177 | 306.4673 | 2005-02-19 | 8217.4849 | 41.7125 | 2005-03-19 | 7646.3439 | 42.494 | 2005-04-19 | -27.3559 | 4959.5083 | 2005-05-19 | 0 | 0 | 2005-06-19 | 7646.3439 | 42.494 | 2005-07-19 | 7553.2519 | 49.1992 | 2005-08-19 | 7806.0774 | 48.3765 | 2005-09-19 |  |  | 2005-10-19 | 7488.6673 | 47.8006 | 2005-11-19 | 8099.5054 | 36.4057 | 2005-12-19 | 8226.3293 | 54.3825
2005-01-20 |  |  | 2005-02-20 | 8196.5052 | 40.067 | 2005-03-20 | 7623.4308 | 42.0004 | 2005-04-20 | -27.4382 | 41.589 | 2005-05-20 | 7922.3105 | 51.773 | 2005-06-20 | 7623.4308 | 42.0004 | 2005-07-20 | 7573.7791 | 50.2689 | 2005-08-20 | 0 | 0 | 2005-09-20 |  |  | 2005-10-20 | 7460.9001 | 48.3354 | 2005-11-20 | 7874.8986 | 35.5009 | 2005-12-20
2005-01-21 | 8014.7225 | 37.2697 | 2005-02-21 | 8235.9554 | 38.0924 | 2005-03-21 | 7747.9102 | 43.1111 | 2005-04-21 | -27.8495 | 42.0826 | 2005-05-21 | 0 | 0 | 2005-06-21 | 7747.9102 | 43.1111 | 2005-07-21 | 7504.5463 | 49.3227 | 2005-08-21 | 7922.3105 | 51.773 | 2005-09-21 |  |  | 2005-10-21 | 7456.1696 | 48.0886 | 2005-11-21 | 8202.3466 | 39.4499 | 2005-12-21 | 0 | 0
2005-01-22 | 8103.2075 | 38.586 | 2005-02-22 | 8259.5268 | 41.1776 | 2005-03-22 | 7823.1079 | 42.2883 | 2005-04-22 | -27.9318 | 40.3137 | 2005-05-22 | 0 | 0 | 2005-06-22 | 7823.1079 | 42.2883 | 2005-07-22 | 7528.4877 | 49.0759 | 2005-08-22 | 8099.5054 | 36.4057 | 2005-09-22 |  |  | 2005-10-22 | 7776.0067 | 48.0886 | 2005-11-22 | 8217.4849 | 41.7125 | 2005-12-22 | 0 | 0
2005-01-23 | 8052.3216 | 38.8328 | 2005-02-23 | 8270.0985 | 42.0827 | 2005-03-23 | 7705.9508 | 40.0669 | 2005-04-23 | -27.7261 | 42.2883 | 2005-05-23 | 0 | 0 | 2005-06-23 | 7705.9508 | 40.0669 | 2005-07-23 | 7521.8648 | 48.3766 | 2005-08-23 | 7874.8986 | 35.5009 | 2005-09-23 |  |  | 2005-10-23 | 7810.2732 | 49.0347 | 2005-11-23 | 8196.5052 | 40.067 | 2005-12-23 | 0 | 0
2005-01-24 | 8048.3313 | 35.8299 | 2005-02-24 | 8175.7723 | 42.3706 | 2005-03-24 | 7609.6914 | 39.9025 | 2005-04-24 | -27.8084 | 42.3706 | 2005-05-24 |  |  | 2005-06-24 | 7609.6914 | 39.9025 | 2005-07-24 | 7546.7113 | 48.2943 | 2005-08-24 | 8202.3466 | 39.4499 | 2005-09-24 |  |  | 2005-10-24 | 7806.0774 | 48.3765 | 2005-11-24 |  |  | 2005-12-24 | 7969.5134 | 53.3541
2005-01-25 | 8076.5922 | 36.5292 | 2005-02-25 | 8119.6619 | 39.6556 | 2005-03-25 | 7639.5976 | 41.2599 | 2005-04-25 | -27.3148 | 42.9465 | 2005-05-25 |  |  | 2005-06-25 | 7639.5976 | 41.2599 | 2005-07-25 | 7488.6673 | 47.8006 | 2005-08-25 | 8217.4849 | 41.7125 | 2005-09-25 |  |  | 2005-10-25 | 0 | 0 | 2005-11-25 |  |  | 2005-12-25 | 7970.4185 | 53.2718
2005-01-26 | 8138.4616 | 40.2315 | 2005-02-26 | 8134.8414 | 40.3961 | 2005-03-26 | 7560.3273 | 40.1903 | 2005-04-26 | -27.685 | 819.276 | 2005-05-26 | 7424.3711 | 47.1013 | 2005-06-26 | 7560.3273 | 40.1903 | 2005-07-26 | 7460.9001 | 48.3354 | 2005-08-26 | 8196.5052 | 40.067 | 2005-09-26 |  |  | 2005-10-26 | 7922.3105 | 51.773 | 2005-11-26 |  |  | 2005-12-26
2005-01-27 | 8112.3403 | 35.4187 | 2005-02-27 | 8246.6508 | 39.4088 | 2005-03-27 | 7481.2219 | 40.5606 | 2005-04-27 | -27.2736 | 48.6645 | 2005-05-27 | 7435.7248 | 47.924 | 2005-06-27 | 7481.2219 | 40.5606 | 2005-07-27 | 7433.2567 | 40.067 | 2005-08-27 |  |  | 2005-09-27 |  |  | 2005-10-27 | 7364.1469 | -4.2783 | 2005-11-27 |  |  | 2005-12-27 | 0 | 0
2005-01-28 | 8141.959 | 34.4313 | 2005-02-28 | 8163.02 | 40.2726 | 2005-03-28 | 7424.1243 | 40.6841 | 2005-04-28 | -27.685 | 2939.7844 | 2005-05-28 | 7433.8646 | 47.3946 | 2005-06-28 | 7424.1243 | 40.6841 | 2005-07-28 | 7451.6857 | 40.2727 | 2005-08-28 |  |  | 2005-09-28 |  |  | 2005-10-28 | -34.2257 | 6734.2638 | 2005-11-28 | 7433.2567 | 40.067 | 2005-12-28 | 8201.1943 | 52.2024
2005-01-29 | 7964.2476 | 34.4313 |  |  |  | 2005-03-29 | 7588.506 | 42.782 | 2005-04-29 | -26.8211 | 6995.8512 | 2005-05-29 | 7491.6293 | 47.8418 | 2005-06-29 | 7588.506 | 42.782 | 2005-07-29 | 7512.7325 | 42.6586 | 2005-08-29 |  |  | 2005-09-29 |  |  | 2005-10-29 | 0 | 0 | 2005-11-29 | 7451.6857 | 40.2727 | 2005-12-29 | 0 | 0
2005-01-30 | 8100.4917 | 37.393 |  |  |  | 2005-03-30 | 7785.9205 | 41.301 | 2005-04-30 | -27.6439 | 6967.3437 | 2005-05-30 | 7491.6293 | 47.8418 | 2005-06-30 | 7785.9205 | 41.301 | 2005-07-30 | 7785.9205 | 41.301 | 2005-08-30 |  |  | 2005-09-30 |  |  | 2005-10-30 | -33.8966 | 6167.9775 | 2005-11-30 | 7512.7325 | 42.6586 | 2005-12-30 | 2120.4263 | 5376.3041
2005-01-31 | 8100.4917 | 37.393 |  |  |  | 2005-03-31 | 7771.5227 | 41.5479 |  |  |  | 2005-05-31 | 1925.5621 | 5125.083 |  |  |  | 2005-07-31 | 7771.5227 | 41.5479 | 2005-08-31 | [5 empty] | 2005-10-31 | [5 empty] | 2005-12-31 | 8170.6302 | 54.7527
K-503 ratio = |  | 0.92589 | K-503 ratio = |  | 1 | K-503 ratio = |  | 1 | K-503 ratio = |  | 0.88335 | K-503 ratio = |  | 0 | K-503 ratio = |  | 0.0013551 | K-503 ratio = |  | 0.2139 | K-503 ratio = |  | 0.98373 | K-503 ratio = |  | 0.14062 | K-503 ratio = |  | 0.41896 | K-503 ratio = |  | 0.13744 | K-503 ratio = |  | 0.12016
Normal Running |  |  | Normal Running |  |  | Normal Running |  |  | Normal Running |  |  | Normal Running |  |  | Normal Running |  |  | Normal Running |  |  | Normal Running |  |  | Normal Running |  |  | Normal Running |  |  | Normal Running |  |  | Normal Running
Date | K-503 | K-504-315 | Date | K-503 | K-504-315 | Date | K-503 | K-504-315 | Date | K-503 | K-504-315 | Date | K-503 | K-504-400 | Date | K-503 | K-504-400 | Date | K-503 | K-504-400 | Date | K-503 | K-504-400 | Date | K-503 | K-504-400 | Date | K-503 | K-504-400 | Date | K-503 | K-504-400 | Date | K-503 | K-504-400
| FC5044 | FC5043 |  | FC5044 | FC5043 |  | FC5044 | FC5043 |  | FC5044 | FC5043 |  | FC5044 | FC5043 |  | FC5044 | FC5043 |  | FC5044 | FC5043 |  | FC5044 | FC5043 |  | FC5044 | FC5043 |  | FC5044 | FC5043 |  | FC5044 | FC5043 |  | FC5044 | FC5043
| M3/Hr | M3/Hr |  | M3/Hr | M3/Hr |  | M3/Hr | M3/Hr |  | M3/Hr | M3/Hr |  | M3/Hr | M3/Hr |  | M3/Hr | M3/Hr |  | M3/Hr | M3/Hr |  | M3/Hr | M3/Hr |  | M3/Hr | M3/Hr |  | M3/Hr | M3/Hr |  | M3/Hr | M3/Hr |  | M3/Hr | M3/Hr
2006-01-01 | 8190.7735 | 55.8223 | 2006-02-01 | 8379.8099 | 54.9173 | 2006-03-01 | 8315.9248 | 48.7879 | 2006-04-01 | 8432.3 | 53.5598 | 2006-05-01 |  |  | 2006-06-01 | -36.2825 | 8706.8046 | 2006-07-01 | -35.7889 | 8744.3623 | 2006-08-01 |  |  | 2006-09-01 |  |  | 2006-10-01 | 1776.8122 | 8674.3889 | 2006-11-01 | -33.0739 | 8995.1719 | 2006-12-01 | -1.6044 | 8918.5758
2006-01-02 | 8301.6507 | 57.583 | 2006-02-02 | 8363.3551 | 53.5598 | 2006-03-02 | 8268.5766 | 50.4745 | 2006-04-02 | 8346.8595 | 54.7939 | 2006-05-02 |  |  | 2006-06-02 | -36.4882 | 8613.1366 | 2006-07-02 | -35.7477 | 8810.4274 | 2006-08-02 |  |  | 2006-09-02 |  |  | 2006-10-02 | 503.6351 | 8670.1108 | 2006-11-02 | -33.4029 | 9005.6208 | 2006-12-02 | 2646.3161 | 8722.1486
2006-01-03 | 8248.5431 | 52.9838 | 2006-02-03 | 8398.1977 | 54.2179 | 2006-03-03 | 8418.1492 | 49.8986 | 2006-04-03 | 8358.501 | 54.9173 | 2006-05-03 | -35.3363 | 9267.9486 | 2006-06-03 | -36.4471 | 8757.0323 | 2006-07-03 | -35.6243 | 8824.1671 | 2006-08-03 | 7912.1275 | 15.7141 | 2006-09-03 |  |  | 2006-10-03 | -31.593 | 8765.3419 | 2006-11-03 | -33.3207 | 8936.6345 | 2006-12-03 | 6999.5536 | 9073.8663
2006-01-04 | 8189.1417 | 53.2306 | 2006-02-04 | 8394.9894 | 53.4775 | 2006-03-04 | 8383.7178 | 53.4363 | 2006-04-04 | 8428.7626 | 55.452 | 2006-05-04 | -35.4598 | 9143.7162 | 2006-06-04 | -36.3237 | 8685.7427 | 2006-07-04 | -35.7066 | 8753.1244 | 2006-08-04 | 7922.8231 | 16.7836 | 2006-09-04 |  |  | 2006-10-04 | -31.6341 | 8693.0651 | 2006-11-04 | -33.6086 | 8912.8164 | 2006-12-04
2006-01-05 | 8245.9104 | 51.5029 | 2006-02-05 | 8370.5545 | 53.3541 | 2006-03-05 | 8314.5673 | 51.6674 | 2006-04-05 | 8379.8512 | 52.3668 | 2006-05-05 | -35.3775 | 9099.2064 | 2006-06-05 | -36.4471 | 8700.8809 | 2006-07-05 | -35.4598 | 8795.7006 | 2006-08-05 | 7908.7957 | 14.768 | 2006-09-05 |  |  | 2006-10-05 | -31.9221 | 8632.0596 | 2006-11-05 | -33.6909 | 8877.9739 | 2006-12-05 | -32.9093 | 8929.8473
2006-01-06 | 8169.1494 | 54.3414 | 2006-02-06 | 8286.1007 | 50.9682 | 2006-03-06 | 8348.0936 | 50.6801 | 2006-04-06 | 8386.5562 | 54.0534 | 2006-05-06 | -35.542 | 9018.6611 | 2006-06-06 | -36.4882 | 8800.8017 | 2006-07-06 | -35.7889 | 8798.0459 | 2006-08-06 | 7970.0892 | 16.6603 | 2006-09-06 |  |  | 2006-10-06 | -31.7986 | 8646.6629 | 2006-11-06 | -33.8966 | 9001.1778 | 2006-12-06 | -33.1561 | 9003.1115
2006-01-07 | 8212.5896 | 52.737 | 2006-02-07 | 8339.8661 | 53.2718 | 2006-03-07 | 8072.5051 | 53.7905 | 2006-04-07 | 4926.8462 | 2753.1479 | 2006-05-07 | -35.1307 | 9086.3716 | 2006-06-07 | -36.5705 | 8719.1866 | 2006-07-07 | -35.7477 | 8828.7334 | 2006-08-07 | 7943.6794 | 14.1098 | 2006-09-07 |  |  | 2006-10-07 | -31.7164 | 8546.7833 | 2006-11-07 | -33.9377 | 9054.0795 | 2006-12-07 | -33.6909 | 8977.9767
2006-01-08 | 2617.1916 | 1567.5504 | 2006-02-08 | 8361.9066 | 51.0003 | 2006-03-08 | 7545.5988 | 56.8811 | 2006-04-08 | 5191.0254 | 2791.7339 | 2006-05-08 | -34.8976 | 8851.4272 | 2006-06-08 | -36.2414 | 8787.3498 | 2006-07-08 | -35.4598 | 8722.3542 | 2006-08-08 | 7939.8539 | 16.5368 | 2006-09-08 |  |  | 2006-10-08 | -32.0455 | 8535.9645 | 2006-11-08 | -33.7732 | 8999.4091 | 2006-12-08 | -33.7732 | 9032.2362
2006-01-09 | 4314.8985 | 3794.5204 | 2006-02-09 | 8331.6873 | 47.0512 | 2006-03-09 | 7517.9982 | 54.6705 | 2006-04-09 | 8326.538 | 53.6009 | 2006-05-09 | -35.1718 | 7480.1939 | 2006-06-09 | -36.1591 | 8775.6259 | 2006-07-09 | -35.0895 | 8846.6278 | 2006-08-09 |  |  | 2006-09-09 |  |  | 2006-10-09 | -32.0168 | 8543.3512 | 2006-11-09 | -33.6909 | 8739.3436 | 2006-12-09 | -34.1023 | 9058.1519
2006-01-10 | 8254.3023 | 52.4902 | 2006-02-10 | 8342.0877 | 50.4745 | 2006-03-10 | 8142.2461 | 51.5029 | 2006-04-10 | 8358.3365 | 54.9584 | 2006-05-10 |  |  | 2006-06-10 | -36.2002 | 8723.3414 | 2006-07-10 | -35.1718 | 8879.0022 | 2006-08-10 | 7961.1698 | 13.6984 | 2006-09-10 |  |  | 2006-10-10 | -32.0598 | 8833.7396 | 2006-11-10 | -33.7732 | 8868.2657 | 2006-12-10 | 3086.1898 | 9070.5341
2006-01-11 | 8288.281 | 55.6166 | 2006-02-11 | 8338.3408 | 52.2452 | 2006-03-11 | 8134.8826 | 55.2463 | 2006-04-11 | 8332.6673 | 54.4236 | 2006-05-11 | -34.7399 | 8525.7008 | 2006-06-11 | -36.118 | 8490.4674 | 2006-07-11 | -35.3363 | 8810.5924 | 2006-08-11 | 7906.492 | 16.6191 | 2006-09-11 |  |  | 2006-10-11 |  |  | 2006-11-11 |  |  | 2006-12-11 | 7730.7157 | 9103.9783
2006-01-12 | 8253.0682 | 54.5471 | 2006-02-12 | 8300.5808 | 54.6705 | 2006-03-12 | 8148.8279 | 53.8066 | 2006-04-12 | 8248.5431 | 53.1072 | 2006-05-12 | -34.3902 | 8375.3672 | 2006-06-12 | -36.118 | 8697.7135 | 2006-07-12 | -35.3363 | 8786.3626 | 2006-08-12 | 7944.173 | 16.0843 | 2006-09-12 | -30.4287 | 7636.0856 | 2006-10-12 | -32.3334 | 8722.5599 | 2006-11-12 | -34.1023 | 8942.9698 | 2006-12-12
2006-01-13 | 8238.8347 | 53.1072 | 2006-02-13 | 8343.5685 | 56.7273 | 2006-03-13 | 8210.7383 | 55.8634 | 2006-04-13 | 8421.646 | 51.5441 | 2006-05-13 | -38.9975 | 8489.5623 | 2006-06-13 | -36.118 | 8684.961 | 2006-07-13 | -35.4186 | 8790.024 | 2006-08-13 |  |  | 2006-09-13 | 7816.3204 | 7205.237 | 2006-10-13 | -32.1689 | 8667.7661 | 2006-11-13 | -34.4314 | 8932.3975 | 2006-12-13 | 6937.0559 | 8887.4941
2006-01-14 | 8255.4954 | 52.5725 | 2006-02-14 | 8344.0496 | 57.0528 | 2006-03-14 | 8300.8688 | 57.0152 | 2006-04-14 | 8356.0739 | 52.4491 | 2006-05-14 | -35.5009 | 8619.924 | 2006-06-14 | -37.2698 | 8517.576 | 2006-07-14 | -35.2952 | 8856.6651 | 2006-08-14 | 7974.9669 | 17.1304 | 2006-09-14 | 7399.7713 | 8210.0392 | 2006-10-14 | -32.4568 | 8689.3627 | 2006-11-14 | -34.5548 | 8715.1141 | 2006-12-14 | -33.3207 | 8835.3974
2006-01-15 | 8228.9621 | 51.3795 | 2006-02-15 | 8384.0555 | 62.0321 | 2006-03-15 | 8337.4803 | 51.2561 | 2006-04-15 | 3137.8574 | 3937.4289 | 2006-05-15 | -37.4344 | 8622.5568 | 2006-06-15 | -35.8711 | 8515.8894 | 2006-07-15 | -35.5009 | 8809.6049 | 2006-08-15 | 7972.9277 | 16.5368 | 2006-09-15 | 2446.3512 | 8274.6238 | 2006-10-15 | -32.2512 | 8728.0721 | 2006-11-15 | -34.6782 | 8844.4067 | 2006-12-15 | -33.732 | 9168.686
2006-01-16 | 8259.3209 | 51.4618 | 2006-02-16 | 8389.2713 | 57.1386 | 2006-03-16 | 8315.4311 | 53.1484 | 2006-04-16 | -2.8797 | 5999.1941 | 2006-05-16 | -34.5548 | 8597.0932 | 2006-06-16 | -35.4598 | 8739.9193 | 2006-07-16 | -35.213 | 8837.1254 | 2006-08-16 | 7965.6876 | 17.6064 | 2006-09-16 | -30.4823 | 8296.3025 | 2006-10-16 | -32.3334 | 8684.6731 | 2006-11-16 | -34.8016 | 9019.8538 | 2006-12-16 | -34.0611 | 9214.5122
2006-01-17 | 8271.7439 | 51.832 | 2006-02-17 | 8256.3177 | 54.3825 | 2006-03-17 | 8406.7955 | 52.5725 | 2006-04-17 | -3.3322 | 5853.7763 | 2006-05-17 | -33.4853 | 8638.9294 | 2006-06-17 | -35.9123 | 8748.0646 | 2006-07-17 | -35.542 | 8878.7143 | 2006-08-17 | 7964.0833 | 17.4007 | 2006-09-17 | 1977.3944 | 8254.22 | 2006-10-17 | -32.3746 | 8746.6247 | 2006-11-17 | -34.925 | 9082.7518 | 2006-12-17 | -34.2943 | 8032.2606
2006-01-18 | 8258.9505 | 52.2022 | 2006-02-18 | 8373.2281 | 52.4902 | 2006-03-18 | 8481.7874 | 56.0279 | 2006-04-18 |  |  | 2006-05-18 | -36.7762 | 8816.8862 | 2006-06-18 | -35.7889 | 8368.9086 | 2006-07-18 | -35.6243 | 8843.2958 | 2006-08-18 | 7936.8507 | 16.1666 | 2006-09-18 | 5658.4191 | 8363.2731 | 2006-10-18 | -32.8134 | 8680.6828 | 2006-11-18 | -34.7193 | 9069.1767 | 2006-12-18 | -34.3902 | 5028.3301
2006-01-19 | 8404.7797 | 54.2179 | 2006-02-19 | 8364.2602 | 49.6106 | 2006-03-19 | 8402.6819 | 52.2845 | 2006-04-19 |  |  | 2006-05-19 | -36.4471 | 8768.098 | 2006-06-19 |  |  | 2006-07-19 | -35.4186 | 8923.5942 | 2006-08-19 | 8059.7258 | 17.3184 | 2006-09-19 | -30.6468 | 8415.7222 | 2006-10-19 | -32.498 | 8619.9654 | 2006-11-19 | -35.0073 | 9113.3162 | 2006-12-19 | 2297.8482 | 8462.4122
2006-01-20 | 8448.0141 | 56.2337 | 2006-02-20 | 8323.3707 | 52.0377 | 2006-03-20 | 8350.7676 | 53.0661 | 2006-04-20 |  |  | 2006-05-20 | -43.2346 | 8818.8195 | 2006-06-20 | -35.6243 | 8713.0982 | 2006-07-20 | -35.7889 | 8857.1589 | 2006-08-20 | 8037.8415 | 18.1823 | 2006-09-20 | -31.3462 | 8430.449 | 2006-10-20 | -32.498 | 8788.4607 | 2006-11-20 | -35.0896 | 9103.7725 | 2006-12-20 | 2628.3805 | 9168.8093
2006-01-21 | 8362.9438 | 54.0534 | 2006-02-21 | 8292.7649 | 53.2306 | 2006-03-21 | 8364.7129 | 52.9838 | 2006-04-21 |  |  | 2006-05-21 | -45.6617 | 8726.55 | 2006-06-21 | -35.7066 | 8783.3599 | 2006-07-21 | -35.3363 | 8842.0617 | 2006-08-21 | 8017.3552 | 17.1539 | 2006-09-21 | -31.3461 | 8484.4202 | 2006-10-21 | -32.5391 | 8725.892 | 2006-11-21 | -35.542 | 9079.8725 | 2006-12-21 | -33.8143 | 9041.6562
2006-01-22 | 8140.7653 | 52.2434 | 2006-02-22 | 8354.0995 | 51.215 | 2006-03-22 | 8347.888 | 52.2845 | 2006-04-22 |  |  | 2006-05-22 | -45.0661 | 8764.4584 | 2006-06-22 | -35.542 | 8757.1967 | 2006-07-22 | -35.4598 | 8860.9433 | 2006-08-22 | 7949.0685 | 16.7013 | 2006-09-22 | -31.1816 | 8665.2977 | 2006-10-22 | -32.7448 | 8652.7512 | 2006-11-22 | -35.1307 | 8963.0031 | 2006-12-22 | -34.2257 | 9020.1419
2006-01-23 | 6483.907 | 620.9566 | 2006-02-23 | 8307.245 | 53.4775 | 2006-03-23 | 8337.4806 | 51.3384 | 2006-04-23 |  |  | 2006-05-23 | -36.3237 | 8806.1493 | 2006-06-23 | -35.9945 | 8805.4911 | 2006-07-23 | -35.3775 | 8811.9495 | 2006-08-23 | 7946.949 | 16.9607 | 2006-09-23 | -31.2227 | 8638.9702 | 2006-10-23 | -32.9183 | 8664.3142 | 2006-11-23 | 2311.2176 | 8833.2996 | 2006-12-23 | -34.2668 | 9094.558
2006-01-24 | 4450.0732 | 3284.18 | 2006-02-24 | 8305.1059 | 53.3952 | 2006-03-24 | 8397.5809 | 51.7497 | 2006-04-24 |  |  | 2006-05-24 | -36.5705 | 8758.5132 | 2006-06-24 | -35.6243 | 8805.409 | 2006-07-24 |  |  | 2006-08-24 | 7948.5748 | 15.7552 | 2006-09-24 | -31.4696 | 8662.7471 | 2006-10-24 | -32.8271 | 8661.6778 | 2006-11-24 | 7000.047 | 8904.4247 | 2006-12-24 | -34.2668 | 8742.0996
2006-01-25 | 8255.3304 | 49.0347 | 2006-02-25 | 8258.7039 | 51.4207 | 2006-03-25 | 8385.7336 | 50.5156 | 2006-04-25 |  |  | 2006-05-25 | -36.5705 | 8700.4696 | 2006-06-25 | -35.6655 | 8725.1927 | 2006-07-25 | 7074.402 | 1100.6297 | 2006-08-25 | 8018.8361 | 18.0178 | 2006-09-25 | -31.593 | 8618.8134 | 2006-10-25 | -32.5803 | 8577.3889 | 2006-11-25 | 6999.5125 | 8946.384 | 2006-12-25 | -34.02 | 8704.2542
2006-01-26 | 8336.6165 | 48.8702 | 2006-02-26 | 8208.0235 | 51.0916 | 2006-03-26 | 8367.7567 | 54.5059 | 2006-04-26 |  |  | 2006-05-26 | -36.2414 | 8504.9883 | 2006-06-26 | -35.9534 | 8739.179 | 2006-07-26 | 8018.8775 | 18.9639 | 2006-08-26 | 7366.4919 | 17.3184 | 2006-09-26 | -31.5107 | 8720.5443 | 2006-10-26 | -32.9505 | 8459.5737 | 2006-11-26 | 6999.3889 | 8897.1023 | 2006-12-26 | 5.0186 | 8826.0597
2006-01-27 | 8323.4939 | 48.5822 | 2006-02-27 | 8237.5596 | 53.7655 | 2006-03-27 | 8292.1478 | 55.4521 | 2006-04-27 |  |  | 2006-05-27 | -36.6116 | 8638.2709 | 2006-06-27 | -35.6655 | 8740.8245 | 2006-07-27 | 8022.991 | 18.4703 | 2006-08-27 | 7050.3984 | 15.0559 | 2006-09-27 | -31.6341 | 8702.403 | 2006-10-27 | -32.8271 | 8742.7579 | 2006-11-27 | 7001.1167 | 8879.6605 | 2006-12-27 | 206.9992 | 8980.7743
2006-01-28 | 8346.3659 | 48.9525 | 2006-02-28 | 8330.4872 | 50.1455 | 2006-03-28 | 8067.5003 | 47.8007 | 2006-04-28 |  |  | 2006-05-28 | -36.2825 | 8806.355 | 2006-06-28 | -36.118 | 8740.2486 | 2006-07-28 | 8037.4713 | 16.8248 | 2006-08-28 | 7044.9271 | 14.2743 | 2006-09-28 | -31.3461 | 8659.0861 | 2006-10-28 | -32.8271 | 8742.7579 | 2006-11-28 | 6998.6074 | 9024.2968 | 2006-12-28
2006-01-29 | 8256.5649 | 51.9143 |  |  |  | 2006-03-29 | 8389.1889 | 53.1484 | 2006-04-29 |  |  | 2006-05-29 | -36.4471 | 8802.2413 | 2006-06-29 |  |  | 2006-07-29 | 8034.0568 | 19.0051 | 2006-08-29 | 7029.0073 | 15.4262 | 2006-09-29 | -31.6752 | 8678.3379 | 2006-10-29 | -32.8682 | 8955.6809 | 2006-11-29 | 4085.3559 | 8969.3794 | 2006-12-29 | -33.8143 | 8791.6695
2006-01-30 | 8212.7131 | 52.1612 |  |  |  | 2006-03-30 | 8416.1746 | 54.0945 | 2006-04-30 |  |  | 2006-05-30 | 0 | 8820.1361 | 2006-06-30 | 330.1211 | 8779.2459 | 2006-07-30 | 7972.4752 | 16.8248 | 2006-08-30 | 3236.4615 | 5997.1378 | 2006-09-30 | 810.6785 | 8641.2739 | 2006-10-30 | -33.0327 | 8988.837 | 2006-11-30 | 7.4868 | 9070.3698 | 2006-12-30 | -33.732 | 8817.4618
2006-01-31 | 8256.5234 | 53.3952 |  |  |  | 2006-03-31 | 8351.9195 | 53.3952 |  |  |  | 2006-05-31 | 0 | 8839.9223 |  |  |  | 2006-07-31 | 8052.3627 | 18.2234 | 2006-08-31 | [5 empty] | 2006-10-31 | -33.1561 | 8985.2992 |  |  |  | 2006-12-31
K-503 ratio = |  | 0.92589 | K-503 ratio = |  | 1 | K-503 ratio = |  | 1 | K-503 ratio = |  | 0.88335 | K-503 ratio = |  | 0 | K-503 ratio = |  | 0.0013551 | K-503 ratio = |  | 0.2139 | K-503 ratio = |  | 0.98373 | K-503 ratio = |  | 0.14062 | K-503 ratio = |  | 0.006807 | K-503 ratio = |  | 0.13744 | K-503 ratio = |  | 0.12016
Normal Running |  |  | Normal Running |  |  | Normal Running |  |  | Normal Running |  |  | Normal Running |  |  | Normal Running |  |  | Normal Running |  |  | Normal Running |  |  | Normal Running |  |  | Normal Running |  |  | Normal Running |  |  | Normal Running
Date | K-503 | K-504-400 | Date | K-503 | K-504-400 | Date | K-503 | K-504-400 | Date | K-503 | K-504-400 | Date | K-503 | K-504-400 | Date | K-503 | K-504-400 | Date | K-503 | K-504-400 | Date | K-503 | K-504-400 | Date | K-503 | K-504-400 | Date | K-503 | K-504-400 | Date | K-503 | K-504-400 | Date | K-503 | K-504-400
| FC5044 | FC5043 |  | FC5044 | FC5043 |  | FC5044 | FC5043 |  | FC5044 | FC5043 |  | FC5044 | FC5043 |  | FC5044 | FC5043 |  | FC5044 | FC5043 |  | FC5044 | FC5043 |  | FC5044 | FC5043 |  | FC5044 | FC5043 |  | FC5044 | FC5043 |  | FC5044 | FC5043
| M3/Hr | M3/Hr |  | M3/Hr | M3/Hr |  | M3/Hr | M3/Hr |  | M3/Hr | M3/Hr |  | M3/Hr | M3/Hr |  | M3/Hr | M3/Hr |  | M3/Hr | M3/Hr |  | M3/Hr | M3/Hr |  | M3/Hr | M3/Hr |  | M3/Hr | M3/Hr |  | M3/Hr | M3/Hr |  | M3/Hr | M3/Hr
2007-01-01 | -33.732 | 8895.2098 | 2007-02-01 | -33.3207 | 9110.2312 | 2007-03-01 | -31.5929 | 8815.4463 | 2007-04-01 | -28.8443 | 9130.4926 | 2007-05-01 | -26.6977 | 9145.2382 | 2007-06-01 | -85.3585 | -1.8101 | 2007-07-01 | -84.001 | 8784.5939 | 2007-08-01 | -82.3144 | 8867.6076 | 2007-09-01 | -82.9726 | 9504.1961 | 2007-10-01 | -82.1087 | 8639.8342 | 2007-11-01 | -77.3368 | 8736.5873 | 2007-12-01
2007-01-02 | -34.0948 | 8891.6611 | 2007-02-02 | -33.4441 | 9088.3875 | 2007-03-02 | -31.4695 | 8860.8199 | 2007-04-02 | -28.0552 | 8831.1603 | 2007-05-02 | -26.5332 | 9158.1139 | 2007-06-02 |  |  | 2007-07-02 | -83.5073 | 8765.2185 | 2007-08-02 | -83.4251 | 8865.5097 | 2007-09-02 | -83.7953 | 9504.2373 | 2007-10-02 | -80.1789 | 8632.0345 | 2007-11-02 | -76.185 | 8762.1743 | 2007-12-02
2007-01-03 | -33.8966 | 8892.9474 | 2007-02-03 | -32.9093 | 9029.8912 | 2007-03-03 | -31.3873 | 8974.727 | 2007-04-03 | -28.2609 | 9174.6921 | 2007-05-03 | -26.4509 | 9111.7939 | 2007-06-03 |  |  | 2007-07-03 | -84.3301 | 8777.8474 | 2007-08-03 | -81.903 | 8877.686 | 2007-09-03 | -84.7826 | 9500.8231 | 2007-10-03 | -81.2037 | 8688.1697 | 2007-11-03 | -74.2927 | 8597.4636 | 2007-12-03 | -79.1057 | 8366.6461
2007-01-04 | -58.845 | 8492.8279 | 2007-02-04 | -32.9505 | 8903.6018 | 2007-03-04 | -31.2639 | 9072.4675 | 2007-04-04 | -28.7957 | 9172.0179 | 2007-05-04 | -26.78 | 9049.2656 | 2007-06-04 |  |  | 2007-07-04 | -83.6719 | 8768.9207 | 2007-08-04 | -82.8492 | 8872.3793 | 2007-09-04 | -83.6719 | 9505.0187 | 2007-10-04 | -81.2037 | 8716.307 | 2007-11-04 | -78.3241 | 8723.0945 | 2007-12-04 | -78.7355 | 8437.113
2007-01-05 | -34.6782 | 8204.4388 | 2007-02-05 | -32.9505 | 9014.7118 | 2007-03-05 | -31.5107 | 8830.8313 | 2007-04-05 | -28.9603 | 9099.0009 | 2007-05-05 |  |  | 2007-06-05 | -85.5016 | -1.4971 | 2007-07-05 | -83.3428 | 8820.4648 | 2007-08-05 | -83.4662 | 8891.1373 | 2007-09-05 | -83.8776 | 9495.1048 | 2007-10-05 | -81.6562 | 8785.4165 | 2007-11-05 | -75.7737 | 8663.6523 | 2007-12-05 | -76.7198 | 8478.8668
2007-01-06 | -34.7605 | 8322.6298 | 2007-02-06 | -33.0739 | 8529.9995 | 2007-03-06 | -31.2639 | 8980.6918 | 2007-04-06 | -28.9603 | 9108.4209 | 2007-05-06 |  |  | 2007-06-06 | -84.906 | 0.4524 | 2007-07-06 | -83.3428 | 8848.7257 | 2007-08-06 | -82.5201 | 8895.4569 | 2007-09-06 | -83.4251 | 9501.1932 | 2007-10-06 | -81.5328 | 8771.0599 | 2007-11-06 | -72.1947 | 8733.0912 | 2007-12-06 | -75.3623 | 6051.7672
2007-01-07 | -34.9662 | 8394.5367 | 2007-02-07 | -33.0739 | 9146.1432 | 2007-03-07 | -31.2227 | 8807.0131 | 2007-04-07 | -29.1248 | 9130.2232 | 2007-05-07 |  |  | 2007-06-07 | -84.4123 | 4375.1223 | 2007-07-07 | -83.8364 | 8830.749 | 2007-08-07 | -84.0833 | 8891.8781 | 2007-09-07 | -81.8207 | 9316.4075 | 2007-10-07 | -82.0676 | 8826.5942 | 2007-11-07 | -77.9389 | 8700.309 | 2007-12-07 | -76.5964 | 4496.7223
2007-01-08 | -35.1307 | 8491.0842 | 2007-02-08 | -32.8682 | 9029.521 | 2007-03-08 | -30.9348 | 8873.4077 | 2007-04-08 | -29.1248 | 9000.4785 | 2007-05-08 | -25.0523 | 9270.9105 | 2007-06-08 | -84.5358 | 10194.3858 | 2007-07-08 | -83.3839 | 8826.0184 | 2007-08-08 | -83.6307 | 8885.7076 | 2007-09-08 | -83.3428 | 9069.0533 | 2007-10-08 | -81.2037 | 8775.9551 | 2007-11-08 | -78.9823 | 8645.6349 | 2007-12-08 | -76.5964 | 8753.6589
2007-01-09 | -35.3364 | 8553.4474 | 2007-02-09 | -32.9093 | 9144.7034 | 2007-03-09 | -30.8937 | 8856.007 | 2007-04-09 | -29.1248 | 9000.4785 | 2007-05-09 | -24.2295 | 9196.6176 | 2007-06-09 | -85.4408 | 10037.7783 | 2007-07-09 | -83.0137 | 8740.3309 | 2007-08-09 | 10.7365 | 10.7365 | 2007-09-09 | -83.713 | 8853.7035 | 2007-10-09 | -78.4475 | 8773.446 | 2007-11-09 | -75.9793 | 8601.2895 | 2007-12-09 | -78.9823 | 8497.4192
2007-01-10 | -35.5832 | 8723.712 | 2007-02-10 | -33.1973 | 9183.2072 | 2007-03-10 | -31.0993 | 8853.2096 | 2007-04-10 | -29.0425 | 9149.434 | 2007-05-10 | -25.4225 | 9146.9659 | 2007-06-10 | -85.4408 | 10193.5217 | 2007-07-10 | -82.3966 | 8786.1981 | 2007-08-10 | -84.4124 | -84.4124 | 2007-09-10 | -83.6719 | 8790.929 | 2007-10-10 | -80.7101 | 8690.967 | 2007-11-10 | -77.4191 | 8607.2542 | 2007-12-10 | -76.8843 | 8500.5866
2007-01-11 | -35.7889 | 8779.7807 | 2007-02-11 | -32.7448 | 9245.9817 | 2007-03-11 | -30.8936 | 8877.7271 | 2007-04-11 | -28.9603 | 9060.3732 | 2007-05-11 | -25.9573 | 9040.7926 | 2007-06-11 | -84.0421 | 9063.0392 | 2007-07-11 | -81.7384 | 8805.2446 | 2007-08-11 | -83.384 | -83.384 | 2007-09-11 | -82.6435 | 8972.67 | 2007-10-11 | -79.7639 | 8706.969 | 2007-11-11 | -77.6659 | 8598.9033 | 2007-12-11 | -76.8843 | 8505.2352
2007-01-12 | -35.7888 | 8664.1458 | 2007-02-12 | -33.1973 | 9175.885 | 2007-03-12 | -30.9759 | 8890.3561 | 2007-04-12 | -28.302 | 9080.5715 | 2007-05-12 | -25.7516 | 8927.1733 | 2007-06-12 | -83.7953 | 8651.0646 | 2007-07-12 | -82.3966 | 8782.2901 | 2007-08-12 | -83.5896 | -83.5896 | 2007-09-12 | -83.096 | 8965.5535 | 2007-10-12 | -80.8334 | 8797.7575 | 2007-11-12 | -77.5837 | 8609.1873 | 2007-12-12 | -74.3339 | 8524.0348
2007-01-13 | -35.2952 | 8454.1437 | 2007-02-13 | -33.1562 | 9231.7072 | 2007-03-13 | -30.5234 | 8821.5755 | 2007-04-13 | -27.6027 | 9037.1724 | 2007-05-13 | -25.6693 | 9011.9145 | 2007-06-13 | -83.5485 | 8695.5332 | 2007-07-13 | -82.1498 | 8975.8376 | 2007-08-13 | -83.9598 | -83.9598 | 2007-09-13 | -82.7669 | 8778.5466 | 2007-10-13 | -80.71 | 8752.3014 | 2007-11-13 | -78.8178 | 8601.0015 | 2007-12-13 | -75.9793 | 8515.0669
2007-01-14 | -35.5009 | 8418.4782 | 2007-02-14 | -33.115 | 9130.9638 | 2007-03-14 | -30.6469 | 9057.576 | 2007-04-14 | -28.0141 | 9077.5686 | 2007-05-14 | -26.5743 | 8894.0169 | 2007-06-14 | -84.906 | 8791.0113 | 2007-07-14 | -83.2605 | 8904.8361 | 2007-08-14 | -84.9471 | -84.9471 | 2007-09-14 | -82.6024 | 8598.6564 | 2007-10-14 | -81.0391 | 8828.7743 | 2007-11-14 | -74.1282 | 8593.7614 | 2007-12-14 | -76.0205 | 8553.4886
2007-01-15 | -35.3834 | -35.3834 | 2007-02-15 | -33.0739 | 9144.8269 | 2007-03-15 | -31.1405 | 9047.9915 | 2007-04-15 | -27.7261 | 9018.1672 | 2007-05-15 | -26.4098 | 8987.7673 | 2007-06-15 | -84.2067 | 8719.7214 | 2007-07-15 | -83.096 | 8840.9922 | 2007-08-15 | -84.0833 | -84.0833 | 2007-09-15 | -82.8903 | 8602.9346 | 2007-10-15 | -82.1087 | 8718.7755 | 2007-11-15 | -78.6532 | 8598.204 | 2007-12-15 | -77.5425 | 8546.7421
2007-01-16 | -35.213 | 73.799 | 2007-02-16 | -33.0327 | 9155.6457 | 2007-03-16 | -30.4411 | 9133.2264 | 2007-04-16 | -27.6027 | 9026.9295 | 2007-05-16 | -26.4509 | 8544.6851 | 2007-06-16 | -86.3458 | 8724.4931 | 2007-07-16 | -83.096 | 8926.227 | 2007-08-16 | -83.2194 | -83.2194 | 2007-09-16 | -83.7131 | 8602.3587 | 2007-10-16 | -80.5455 | 8828.4041 | 2007-11-16 | -77.7893 | 8606.1847 | 2007-12-16 | -74.5395 | 8489.274
2007-01-17 |  |  | 2007-02-17 | -32.6214 | 9107.0631 | 2007-03-17 | -30.112 | 9201.0195 | 2007-04-17 | -27.7672 | 9154.1648 | 2007-05-17 | -25.2168 | 8904.5481 | 2007-06-17 | -81.0803 | 8830.0908 | 2007-07-17 | -83.9598 | 8934.4135 | 2007-08-17 | -83.4662 | -83.4662 | 2007-09-17 | -84.4011 | 8601.0423 | 2007-10-17 | -80.5044 | 8830.6259 | 2007-11-17 | -76.6375 | 8616.4274 | 2007-12-17 | -75.2389 | 8574.1391
2007-01-18 |  |  | 2007-02-18 | -32.5391 | 9068.3126 | 2007-03-18 | -29.9886 | 9185.5521 | 2007-04-18 | -27.1913 | 9066.9553 | 2007-05-18 | -25.6693 | 8972.1766 | 2007-06-18 | -85.549 | 8787.0665 | 2007-07-18 | -82.4789 | 8940.2544 | 2007-08-18 | -83.9187 | -83.9187 | 2007-09-18 | -85.6303 | 8607.0519 | 2007-10-18 | -80.8335 | 8793.4794 | 2007-11-18 | -82.6846 | 8612.8906 | 2007-12-18 | -74.8275 | 8537.1984
2007-01-19 |  |  | 2007-02-19 | -32.9093 | 9028.9453 | 2007-03-19 | -30.4412 | 9093.4884 | 2007-04-19 | -28.0141 | 8918.3703 | 2007-05-19 | -24.8877 | 9117.6767 | 2007-06-19 | -82.9314 | 8895.0865 | 2007-07-19 | -83.4662 | 8954.6115 | 2007-08-19 | -84.9883 | -84.9883 | 2007-09-19 | -83.0549 | 8596.682 | 2007-10-19 | -80.5043 | 8851.523 | 2007-11-19 | -79.9696 | 8534.8536 | 2007-12-19 | -74.3339 | 8508.7729
2007-01-20 |  |  | 2007-02-20 | -32.1277 | 9102.0859 | 2007-03-20 | -30.2766 | 9141.8239 | 2007-04-20 | -27.685 | 8923.512 | 2007-05-20 | -25.0934 | 8993.6499 | 2007-06-20 |  |  | 2007-07-20 | -83.5073 | 8995.9945 | 2007-08-20 | -84.5769 | -84.5769 | 2007-09-20 | -83.096 | 8531.3979 | 2007-10-20 | -80.0519 | 8846.4222 | 2007-11-20 | -77.5837 | 8497.4195 | 2007-12-20 | -74.375 | 8438.4707
2007-01-21 |  |  | 2007-02-21 | -31.9632 | 9065.2687 | 2007-03-21 | -29.6184 | 9120.6796 | 2007-04-21 | -27.2737 | 9072.2211 | 2007-05-21 | -24.6409 | 9202.7471 | 2007-06-21 |  |  | 2007-07-21 | -84.4124 | 8959.1776 | 2007-08-21 | -82.9314 | -82.9314 | 2007-09-21 | -82.2732 | 8493.5116 | 2007-10-21 | -78.0361 | 8829.1036 | 2007-11-21 | -78.5298 | 8502.479 | 2007-12-21 | -73.0175 | 8339.2493
2007-01-22 |  |  | 2007-02-22 | -31.7163 | 8920.3856 | 2007-03-22 | -29.3306 | 9104.2663 | 2007-04-22 | -27.4793 | 8612.1493 | 2007-05-22 | -24.8054 | 9020.3473 | 2007-06-22 |  |  | 2007-07-22 | -83.2605 | 9036.432 | 2007-08-22 | -83.9599 | -83.9599 | 2007-09-22 | -82.4789 | 8496.7199 | 2007-10-22 | -78.4887 | 8853.2095 | 2007-11-22 | -78.6121 | 8501.4919 | 2007-12-22 | -74.375 | 8502.9727
2007-01-23 | -33.9377 | 8600.302 | 2007-02-23 | -31.7986 | 8743.6219 | 2007-03-23 | -29.3306 | 8988.5899 | 2007-04-23 | -27.3148 | 8969.7085 | 2007-05-23 | -25.1346 | 8972.2998 | 2007-06-23 | -82.7669 | 8815.2823 | 2007-07-23 | -82.2732 | 8910.4719 | 2007-08-23 | -84.906 | -84.906 | 2007-09-23 | -83.1371 | 7450.9047 | 2007-10-23 | -77.8306 | 8865.88 | 2007-11-23 | -78.5672 | 8501.1029 | 2007-12-23 | -71.2075 | 8533.9072
2007-01-24 | -34.4314 | 8649.4191 | 2007-02-24 | -31.5107 | 8659.374 | 2007-03-24 | -28.9191 | 9058.358 | 2007-04-24 | -27.1914 | 8892.0425 | 2007-05-24 | -24.5175 | 8917.3004 | 2007-06-24 | -84.5769 | 8682.6986 | 2007-07-24 | -82.8903 | 8885.5431 | 2007-08-24 | -83.2194 | -83.2194 | 2007-09-24 | -81.9441 | 8492.2774 | 2007-10-24 | -78.1184 | 8714.0858 | 2007-11-24 | -78.5672 | 8501.1029 | 2007-12-24 | -73.1821 | 8513.1738
2007-01-25 | -34.4725 | 8501.492 | 2007-02-25 | -31.5518 | 8687.9229 | 2007-03-25 | -29.0837 | 9211.1391 | 2007-04-25 | -27.2325 | 8929.9293 | 2007-05-25 | -24.9289 | 8785.8281 | 2007-06-25 | -84.2478 | 8802.982 | 2007-07-25 | -81.3682 | 8588.2899 | 2007-08-25 | -84.1244 | -84.1244 | 2007-09-25 | -81.5739 | 8510.9531 | 2007-10-25 | -74.1693 | 8611.6556 | 2007-11-25 | 2202.3141 | 8809.2683 | 2007-12-25 | -74.4161 | 8503.1781
2007-01-26 | -34.02 | 8709.8899 | 2007-02-26 | -31.9632 | 8746.131 | 2007-03-26 | -28.8368 | 9102.9086 | 2007-04-26 | -27.6439 | 8934.5366 | 2007-05-26 | -24.97 | 8721.0791 | 2007-06-26 | -83.6719 | 8832.4355 | 2007-07-26 | -81.7385 | 8499.5585 | 2007-08-26 | -84.2067 | -84.2067 | 2007-09-26 | -82.0675 | 8524.3639 | 2007-10-26 | -82.2086 | 8556.1918 | 2007-11-26 |  |  | 2007-12-26 | -74.3339 | 8510.5418
2007-01-27 | -34.2257 | 8653.944 | 2007-02-27 | -31.6341 | 8884.926 | 2007-03-27 | -28.7134 | 9246.0639 | 2007-04-27 | -27.397 | 8962.88 | 2007-05-27 | -25.4225 | 8765.7122 | 2007-06-27 | -84.0833 | 8778.1763 | 2007-07-27 | -81.6562 | 8457.9692 | 2007-08-27 | -84.2067 | -84.2067 | 2007-09-27 | -81.9441 | 8601.0835 | 2007-10-27 | -79.6816 | 8729.841 | 2007-11-27 |  |  | 2007-12-27 | -75.6502 | 8502.4381
2007-01-28 | -34.0611 | 8654.0263 | 2007-02-28 | -31.6752 | 8687.9229 | 2007-03-28 | -29.0837 | 9164.12 | 2007-04-28 | -26.5332 | 9033.47 | 2007-05-28 | -25.6693 | 8604.9092 | 2007-06-28 | -79.1469 | 8803.2697 | 2007-07-28 | -82.4789 | 8631.3601 | 2007-08-28 | -83.2194 | -83.2194 | 2007-09-28 |  |  | 2007-10-28 | -79.6816 | 8767.3575 | 2007-11-28 |  |  | 2007-12-28 | -73.3054 | 8502.8081
2007-01-29 | -33.8143 | 8660.0322 |  |  |  | 2007-03-29 | -29.0014 | 9177.4071 | 2007-04-29 | -26.3275 | 9081.1473 | 2007-05-29 | -25.0523 | 8500.8337 | 2007-06-29 | -82.8492 | 8767.5221 | 2007-07-29 | -86.4692 | 8910.8829 | 2007-08-29 | -83.5485 | -83.5485 | 2007-09-29 | -82.1963 | 8600.656 | 2007-10-29 | -77.4603 | 8766.247 | 2007-11-29 |  |  | 2007-12-29 | -72.8118 | 8497.296
2007-01-30 | -33.7732 | 8797.3873 |  |  |  | 2007-03-30 | -28.7134 | 9198.9215 | 2007-04-30 | -26.6155 | 9073.7838 | 2007-05-30 | -25.9573 | 6399.001 | 2007-06-30 | -84.8648 | 8856.2126 | 2007-07-30 | -86.3204 | 8880.2902 | 2007-08-30 | -83.7542 | -83.7542 | 2007-09-30 | -77.954 | 8770.1546 | 2007-10-30 | -75.1566 | 8701.7858 | 2007-11-30 |  |  | 2007-12-30 | -72.3593 | 8513.2567
2007-01-31 | -33.3207 | 9022.4043 |  |  |  | 2007-03-31 | -28.8443 | 9130.4926 |  |  |  | 2007-05-31 | -35.4187 | 162.5305 |  |  |  | 2007-07-31 | -82.9315 | 8870.9808 | 2007-08-31 | -83.4662 | -83.4662 |  |  |  | 2007-10-31 | -76.185 | 8651.9695 |  |  |  | 2007-12-31 | -67.8343 | 8435.1386
K-503 ratio = |  | 0 | K-503 ratio = |  | 0 | K-503 ratio = |  | 0 | K-503 ratio = |  | 0 | K-503 ratio = |  | 0 | K-503 ratio = |  | 0 | K-503 ratio = |  | 0 | K-503 ratio = |  | 0 | K-503 ratio = |  | 0 | K-503 ratio = |  | 0 | K-503 ratio = |  | 0.010222 | K-503 ratio = |  | 0
Normal Running |  |  | Normal Running |  |  | Normal Running |  |  | Normal Running |  |  | Normal Running |  |  | Normal Running |  |  | Normal Running |  |  | Normal Running |  |  | Normal Running |  |  | Normal Running |  |  | Normal Running |  |  | Normal Running
Note on J6: dindin: TPSDDE Error
Note on R12: dindin: TPSDDE Error
Note on AL12: dindin: TPSDDE Error
Note on AD18: dindin: TPSDDE Error
Note on AP20: dindin: TPSDDE Error
Note on AD24: dindin: TPSDDE Error
Note on AT31: dindin: TPSDDE Error
Note on B32: dindin: TPSDDE Error
Note on AT81: turbin K-305 stop K-504 inservice, speed 3795 rpm.
Note on AT82: K-504 normal, danfos temp. 53 °C, 37960 rpm K-503 speed 4109 rpm
Note on N86: K-503 heat up K-504 running
Note on B87: K-504 P/M on MDP
Note on N87: Swapped K-504 to K-503
Note on B88: Power off at 10.35-17.35
Note on AT89: Start K-503 (power dip 2 x)
Note on AT90: K-504 active speed 3980 rpm K-503 active speed 3780 rpm 653 amp.
Note on AT92: Restart SRU
Note on N94: repair K-503 turbine
Note on AT98: K-501 normal danfos temp. 50 °C, 637 amp. Speed 3793 rpm K-503 speed 3890 rpm.
Note on AT99: K-504 speed 3797 rpm, 641 amp.
Note on AP102: 1. K-504 speed 3817 rpm 657 amp. 53 °C K-503 rpm
Note on B103: Swap K-504 to K-503, and keep speed on 4150 rpm
Note on AP103: 1. K-504 normal, danfos temp. 53 °C, speed decrease from 3800 to 3790 rpm. 2. K-503 active, speed 4100 rpm, K-504 speed 4100 rpm 637 amp.
Note on Z104: barlianal: K-504 chnages to K-503, because of plant load down due to storage level high
Note on AP104: 1. K-504 speed 3795 rpm, 631 rpm K-503 active, speed 4105 rpm, 2. K-504 normal, danfos temp. 53 °C 644 amp. Speed 3794 rpm K-503 speed 4100 rpm 3. K-504 speed 3790 rpm, 648 amp. K-503 speed 4100 rpm.
Note on AP105: 1. K-504 speed 3795 rpm, 631 rpm K-503 active, speed 4102 rpm, 2. K-504 normal, danfos temp. 53 °C 644 amp. Speed 3794 rpm K-503 speed 4100 rpm 3. K-504 speed 3790 rpm, 648 amp. K-503 speed 4100 rpm.
Note on AP106: 1. K-504 speed 3780 rpm, 635 rpm K-503 active, speed 4100 rpm,
Note on AP107: 1. K-504 speed 3794 rpm, 640 rpm K-503 active, speed 4105 rpm,
Note on AP108: 1. K-504 speed 3780 rpm, 635 rpm, 635 amp K-503 stop
Note on S109: barlianal: Format TPSDDE bergeser
Note on AI111: ACI : the ratio should consider the amount of steam consumed to run the blower
Note on AQ111: ACI : the ratio should consider the amount of steam consumed to run the blower
Note on AU111: ACI : the ratio should consider the amount of steam consumed to run the blower
Note on AT117: barlianal: TPSDDE data lost
Note on V118: barlianal: TPSDDE error
Note on R121: barlianal: TPSDDE error
Note on B133: barlianal: TPSDDE error
Note on V136: barlianal: TPSDDE error
Note on AP142: barlianal: TPSDDE error
Note on AH144: barlianal: TPSDDE error

## P &T Steam
Year | HP Steam | HP Steam | Year | HP Steam | HP Steam | Year | HP Steam | HP Steam | Year | HP Steam | HP Steam
2004 | (Press.) barg | (Temp.) °C | 2005 | (Press.) barg | (Temp.) °C | 2006 | (Press.) barg | (Temp.) °C | 2007 | (Press.) barg | (Temp.) °C
| PC8501 | TI8502 |  | PC8501 | TI8502 |  | PC8501 | TI8502 |  | PC8501 | TI8502
2004-01-01 | 23.5876 | 224.4136 | 2005-01-01 | 23.5876 | 224.4136 | 2006-01-01 | 23.382 | 224.0364 | 2007-01-01 | 24.2423 | 226.014
2004-01-02 | 22.0045 | 220.7296 | 2005-01-02 | 22.0045 | 220.7296 | 2006-01-02 | 23.8595 | 225.119 | 2007-01-02 | 24.2814 | 226.2778
2004-01-03 | 21.9583 | 220.7256 | 2005-01-03 | 21.9583 | 220.7256 | 2006-01-03 | 23.0919 | 223.3714 | 2007-01-03 | 23.7619 | 224.8083
2004-01-04 | 22 | 220.7123 | 2005-01-04 | 24.0596 | 225.2831 | 2006-01-04 | 23.345 | 222.7041 | 2007-01-04
2004-01-05 | 24.0596 | 225.2831 | 2005-01-05 | 24.0596 | 225.2831 | 2006-01-05 | 23.4466 | 223.2142 | 2007-01-05 | 22.4069 | 222.1832
2004-01-06 | 22.8549 | 222.8587 | 2005-01-06 | 22.8549 | 222.8587 | 2006-01-06 | 23.3788 | 224.5412 | 2007-01-06 | 23.8029 | 224.9896
2004-01-07 | 22.9562 | 222.9523 | 2005-01-07 | 22.9562 | 222.9523 | 2006-01-07 | 23.4469 | 224.7681 | 2007-01-07 | 22.897 | 223.8527
2004-01-08 | 21.9769 | 220.683 | 2005-01-08 | 21.9769 | 220.683 | 2006-01-08 | 11.0367 | 177.9534 | 2007-01-08 | 23.7383 | 224.7358
2004-01-09 | 23.0236 | 223.218 | 2005-01-09 | 23.0236 | 223.218 | 2006-01-09 | 23.1171 | 223.7846 | 2007-01-09 | 23.863 | 225.042
2004-01-10 | 21.9934 | 220.6627 | 2005-01-10 | 21.9934 | 220.6627 | 2006-01-10 | 23.662 | 224.9525 | 2007-01-10
2004-01-11 | 23.068 | 223.3032 | 2005-01-11 | 23.068 | 223.3032 | 2006-01-11 | 23.488 | 223.4896 | 2007-01-11 | 24.1893 | 225.7446
2004-01-12 | 21.998 | 220.636 | 2005-01-12 | 21.998 | 220.636 | 2006-01-12 | 23.6014 | 202.593 | 2007-01-12 | 24.5269 | 226.4048
2004-01-13 | 22.0046 | 220.6317 | 2005-01-13 | 22.0046 | 220.6317 | 2006-01-13 | 23.7058 | 201.7082 | 2007-01-13 | 24.4661 | 226.6047
2004-01-14 | 23.5696 | 224.4209 | 2005-01-14 | 23.5696 | 224.4209 | 2006-01-14 | 23.7901 | 199.586 | 2007-01-14 | 22.0364 | 223.3439
2004-01-15 | 23.7396 | 224.7935 | 2005-01-15 | 23.7396 | 224.7935 | 2006-01-15 | 23.6862 | 197.5395 | 2007-01-15
2004-01-16 | 23.7113 | 224.7157 | 2005-01-16 | 23.7113 | 224.7157 | 2006-01-16 | 23.267 | 197.7371 | 2007-01-16
2004-01-17 | 22.5027 | 221.7252 | 2005-01-17 | 22.5027 | 221.7252 | 2006-01-17 | 23.6431 | 205.1635 | 2007-01-17
2004-01-18 | 1.9373 | 58.9229 | 2005-01-18 | 1.9373 | 58.9229 | 2006-01-18 | 23.6727 | 205.8011 | 2007-01-18
2004-01-19 | 22.493 | 221.7257 | 2005-01-19 | 1.9373 | 58.9229 | 2006-01-19 | 23.5779 | 206.3015 | 2007-01-19
2004-01-20 | 16.0048 | 213.0135 | 2005-01-20 |  |  | 2006-01-20 | 23.7675 | 204.5921 | 2007-01-20
2004-01-21 | 22.1994 | 221.0019 | 2005-01-21 | 22.8529 | 222.9925 | 2006-01-21 | 23.5002 | 201.5 | 2007-01-21
2004-01-22 | 9.2055 | 182.1115 | 2005-01-22 | 23.0793 | 223.5957 | 2006-01-22 | 23.1496 | 203.2448 | 2007-01-22
2004-01-23 | 21.9858 | 220.6289 | 2005-01-23 | 22.6373 | 222.1713 | 2006-01-23 | 21.11 | 198.5035 | 2007-01-23
2004-01-24 | 22.0426 | 220.6403 | 2005-01-24 | 22.8185 | 223.01 | 2006-01-24 | 23.0353 | 200.5453 | 2007-01-24 | 24.1378 | 225.6658
2004-01-25 | 21.9934 | 220.5699 | 2005-01-25 | 22.9077 | 223.2554 | 2006-01-25 | 23.38 | 201.0386 | 2007-01-25 | 23.9778 | 225.296
2004-01-26 | 22.0014 | 220.653 | 2005-01-26 | 23.0868 | 223.5087 | 2006-01-26 | 23.6106 | 202.5563 | 2007-01-26 | 24.0811 | 225.131
2004-01-27 | 21.9785 | 220.609 | 2005-01-27 | 22.7536 | 222.8577 | 2006-01-27 | 23.496 | 202.1186 | 2007-01-27 | 24.4691 | 226.4247
2004-01-28 | 24.203 | 225.7429 | 2005-01-28 | 21.4087 | 219.7266 | 2006-01-28 | 23.802 | 202.4451 | 2007-01-28 | 24.4762 | 226.4062
2004-01-29 | 23.7114 | 224.7376 | 2005-01-29 | 23.8458 | 225.3113 | 2006-01-29 | 23.7634 | 200.9783 | 2007-01-29 | 24.4748 | 226.4158
2004-01-30 | 23.9056 | 226.2024 | 2005-01-30 | 22.5124 | 222.3999 | 2006-01-30 | 23.5382 | 202.3789 | 2007-01-30 | 24.0544 | 225.6584
2004-01-31 | 23.6974 | 224.5679 | 2005-01-31 | 22.5124 | 222.3999 | 2006-01-31 | 23.7817 | 202.748 | 2007-01-31 | 24.492 | 226.4931
2004-02-01 | 23.2226 | 223.1725 | 2005-02-01 | 22.9344 | 223.2727 | 2006-02-01 | 23.595 | 226.8433 | 2007-02-01 | 24.4109 | 226.4053
2004-02-02 | 23.9836 | 225.1981 | 2005-02-02 | 23.2173 | 223.7854 | 2006-02-02 | 23.5077 | 226.8433 | 2007-02-02 | 24.1954 | 225.8331
2004-02-03 | 24.1637 | 225.6905 | 2005-02-03 | 22.9738 | 223.291 | 2006-02-03 | 23.5259 | 224.6384 | 2007-02-03 | 24.3656 | 226.1787
2004-02-04 | 24.0131 | 225.1993 | 2005-02-04 | 22.8575 | 223.1445 | 2006-02-04 | 23.5624 | 224.4881 | 2007-02-04 | 24.3101 | 226.1782
2004-02-05 | 24.1054 | 225.5692 | 2005-02-05 | 22.8575 | 223.1445 | 2006-02-05 | 24.1677 | 225.3894 | 2007-02-05 | 24.3483 | 226.2278
2004-02-06 | 24.1284 | 225.6276 | 2005-02-06 | 23.0035 | 223.4009 | 2006-02-06 | 23.7725 | 225.2225 | 2007-02-06 | 22.6695 | 221.0983
2004-02-07 | 24.0014 | 224.2737 | 2005-02-07 | 23.9017 | 225.2991 | 2006-02-07 | 24.0477 | 225.5221 | 2007-02-07 | 24.4872 | 226.5373
2004-02-08 | 23.589 | 225.6226 | 2005-02-08 | 7.5048 | 173.7091 | 2006-02-08 | 23.7943 | 225.1445 | 2007-02-08 | 24.5099 | 226.6088
2004-02-09 | 24.1214 | 225.3209 | 2005-02-09 | 23.1299 | 223.6389 | 2006-02-09 | 23.6103 | 224.7503 | 2007-02-09 | 24.1721 | 226.0752
2004-02-10 | 23.9852 | 225.323 | 2005-02-10 | 22.8502 | 223.0164 | 2006-02-10 | 23.7141 | 224.9753 | 2007-02-10
2004-02-11 | 23.9087 | 225.1735 | 2005-02-11 | 22.5508 | 222.3816 | 2006-02-11 | 23.6997 | 224.3403 | 2007-02-11 | 24.2802 | 226.1589
2004-02-12 | 23.7996 | 224.9832 | 2005-02-12 | 22.8877 | 223.0164 | 2006-02-12 | 23.6126 | 224.7205 | 2007-02-12 | 24.4937 | 226.5722
2004-02-13 | 24.0762 | 225.459 | 2005-02-13 | 18.9977 | 213.8428 | 2006-02-13 | 23.7525 | 225.1134 | 2007-02-13 | 24.4738 | 226.5383
2004-02-14 | 23.8164 | 225.086 | 2005-02-14 | 24.0051 | 225.5493 | 2006-02-14 | 23.7407 | 225.0825 | 2007-02-14 | 24.5215 | 226.5912
2004-02-15 | 24.0012 | 225.2294 | 2005-02-15 | 23.101 | 223.4802 | 2006-02-15 | 23.9206 | 225.4336 | 2007-02-15 | 24.5176 | 226.575
2004-02-16 | 24.0012 | 225.2294 | 2005-02-16 | 24.2331 | 226.0803 | 2006-02-16 | 23.9326 | 225.5186 | 2007-02-16 | 24.5095 | 226.5399
2004-02-17 | 23.6853 | 224.2869 | 2005-02-17 | 22.9047 | 223.1382 | 2006-02-17 | 23.9137 | 225.4227 | 2007-02-17 | 24.4835 | 226.5284
2004-02-18 | 23.9106 | 225.1984 | 2005-02-18 | 23.3389 | 224.0677 | 2006-02-18 | 23.8288 | 225.2678 | 2007-02-18 | 24.4889 | 226.5086
2004-02-19 | 23.878 | 224.8792 | 2005-02-19 | 23.168 | 223.6852 | 2006-02-19 | 23.428 | 224.9184 | 2007-02-19 | 24.5089 | 226.561
2004-02-20 | 23.6066 | 224.7017 | 2005-02-20 | 23.0009 | 223.469 | 2006-02-20 | 23.5389 | 224.3355 | 2007-02-20 | 24.4979 | 226.5175
2004-02-21 | 24.186 | 225.31 | 2005-02-21 | 23.0156 | 223.4065 | 2006-02-21 | 23.4915 | 224.5895 | 2007-02-21 | 24.495 | 226.6103
2004-02-22 | 23.8153 | 225.0371 | 2005-02-22 | 22.6534 | 222.4622 | 2006-02-22 | 23.5671 | 224.6234 | 2007-02-22 | 24.4992 | 226.5666
2004-02-23 | 19.4034 | 224.1081 | 2005-02-23 | 23.0953 | 223.6995 | 2006-02-23 | 23.7423 | 225.1328 | 2007-02-23 | 24.4971 | 226.5279
2004-02-24 | 23.245 | 223.8767 | 2005-02-24 | 23.2419 | 223.5077 | 2006-02-24 | 23.8564 | 225.4517 | 2007-02-24 | 24.4999 | 226.5005
2004-02-25 | 22.5541 | 222.4342 | 2005-02-25 | 22.6278 | 222.5609 | 2006-02-25 | 23.8777 | 225.3741 | 2007-02-25
2004-02-26 | 22.5541 | 222.4342 | 2005-02-26 | 22.8312 | 222.8935 | 2006-02-26 | 23.6624 | 224.7523 | 2007-02-26 | 24.4802 | 226.4366
2004-02-27 | 23.4762 | 224.5519 | 2005-02-27 | 23.1757 | 222.4246 | 2006-02-27 | 23.6763 | 225.2935 | 2007-02-27 | 24.4993 | 226.5157
2004-02-28 | 23.0238 | 224.6994 | 2005-02-28 | 23.118 | 221.0938 | 2006-02-28 | 24.0755 | 225.5992 | 2007-02-28
2004-02-29 | 22.9509 | 222.638
2004-03-01 | 23.2226 | 223.1725 | 2005-03-01 | 22.3977 | 226.3001 | 2006-03-01 | 23.5348 | 224.6259 | 2007-03-01
2004-03-02 | 23.9836 | 225.1981 | 2005-03-02 | 22.7313 | 223.0273 | 2006-03-02 | 23.5579 | 224.6808 | 2007-03-02
2004-03-03 | 24.1637 | 225.6905 | 2005-03-03 | 21.4888 | 213.5157 | 2006-03-03 | 23.8927 | 225.3827 | 2007-03-03 | 24.5048 | 226.5165
2004-03-04 | 24.0131 | 225.1993 | 2005-03-04 | 22.9694 | 222.8569 | 2006-03-04 | 23.516 | 224.5272 | 2007-03-04 | 24.4759 | 226.5363
2004-03-05 | 24.1054 | 225.5692 | 2005-03-05 | 22.9694 | 222.8569 | 2006-03-05 | 23.6193 | 224.7681 | 2007-03-05 | 23.8105 | 226.3558
2004-03-06 | 24.1284 | 225.6276 | 2005-03-06 | 23.1086 | 224.1618 | 2006-03-06 | 23.3681 | 224.2943 | 2007-03-06 | 24.5177 | 226.4819
2004-03-07 | 24.0014 | 224.2737 | 2005-03-07 | 0 | 0 | 2006-03-07 | 23.5047 | 224.6367 | 2007-03-07 | 24.5646 | 226.5612
2004-03-08 | 23.589 | 225.6226 | 2005-03-08 | 23.1044 | 223.6407 | 2006-03-08 | 23.3836 | 224.3599 | 2007-03-08 | 24.4908 | 226.4183
2004-03-09 | 24.1214 | 225.3209 | 2005-03-09 | 22.7588 | 222.746 | 2006-03-09 | 23.1193 | 223.7999 | 2007-03-09 | 24.5159 | 226.4516
2004-03-10 | 23.9852 | 225.323 | 2005-03-10 | 22.5504 | 222.449 | 2006-03-10 | 23.5545 | 224.9565 | 2007-03-10
2004-03-11 | 23.9087 | 225.1735 | 2005-03-11 | 23.0429 | 223.4434 | 2006-03-11 | 23.4519 | 224.6946 | 2007-03-11 | 24.5088 | 226.5651
2004-03-12 | 23.7996 | 224.9832 | 2005-03-12 | 22.8768 | 223.2213 | 2006-03-12 | 23.3346 | 224.4309 | 2007-03-12 | 24.5265 | 226.5834
2004-03-13 | 24.0762 | 225.459 | 2005-03-13 | 22.3569 | 221.7321 | 2006-03-13 | 23.4337 | 225.4196 | 2007-03-13 | 24.5133 | 226.5437
2004-03-14 | 23.8164 | 225.086 | 2005-03-14 | 20.4952 | 216.7652 | 2006-03-14 | 23.9249 | 225.1122 | 2007-03-14 | 24.512 | 226.5399
2004-03-15 | 24.0012 | 225.2294 | 2005-03-15 | 22.6937 | 222.524 | 2006-03-15 | 23.8082 | 225.0905 | 2007-03-15 | 24.4925 | 226.5086
2004-03-16 | 24.0012 | 225.2294 | 2005-03-16 | 22.9717 | 223.1723 | 2006-03-16 | 23.913 | 225.2408 | 2007-03-16 | 24.4942 | 226.5076
2004-03-17 | 23.6853 | 224.2869 | 2005-03-17 | 22.8403 | 222.9083 | 2006-03-17 | 23.7789 | 225.2218 | 2007-03-17 | 24.4928 | 226.5096
2004-03-18 | 23.9106 | 225.1984 | 2005-03-18 | 23.1584 | 223.6646 | 2006-03-18 | 23.4543 | 223.6188 | 2007-03-18 | 24.4983 | 226.6152
2004-03-19 | 23.878 | 224.8792 | 2005-03-19 | 23.2123 | 223.777 | 2006-03-19 | 23.3181 | 223.9678 | 2007-03-19 | 24.5096 | 226.5612
2004-03-20 | 23.6066 | 224.7017 | 2005-03-20 | 22.8687 | 223.2775 | 2006-03-20 | 23.2372 | 223.8976 | 2007-03-20 | 24.4901 | 226.5356
2004-03-21 | 24.186 | 225.31 | 2005-03-21 | 22.8165 | 222.9309 | 2006-03-21 | 23.6387 | 224.3365 | 2007-03-21 | 24.4921 | 226.5694
2004-03-22 | 23.8153 | 225.0371 | 2005-03-22 | 23.0898 | 223.0848 | 2006-03-22 | 23.7817 | 225.3347 | 2007-03-22 | 24.5054 | 226.5498
2004-03-23 | 19.4034 | 224.1081 | 2005-03-23 | 22.8171 | 223.0385 | 2006-03-23 | 23.6477 | 224.8861 | 2007-03-23 | 24.505 | 226.534
2004-03-24 | 23.245 | 223.8767 | 2005-03-24 | 23.1317 | 223.5474 | 2006-03-24 | 23.8268 | 225.2594 | 2007-03-24 | 24.4866 | 226.5172
2004-03-25 | 22.5541 | 222.4342 | 2005-03-25 | 22.9326 | 223.8991 | 2006-03-25 | 23.6653 | 224.8416 | 2007-03-25 | 24.5344 | 226.5414
2004-03-26 | 22.5541 | 222.4342 | 2005-03-26 | 22.8513 | 223.0583 | 2006-03-26 | 23.7393 | 225.2792 | 2007-03-26 | 24.5193 | 226.502
2004-03-27 | 23.4762 | 224.5519 | 2005-03-27 | 22.3761 | 221.8559 | 2006-03-27 | 23.6953 | 224.6747 | 2007-03-27 | 24.5041 | 226.4638
2004-03-28 | 23.0238 | 224.6994 | 2005-03-28 | 23.0104 | 223.3955 | 2006-03-28 | 24.059 | 222.7216 | 2007-03-28 | 24.5087 | 226.4323
2004-03-29 | 22.9509 | 222.638 | 2005-03-29 | 23.3417 | 224.1356 | 2006-03-29 | 23.6791 | 224.7223 | 2007-03-29 | 24.4983 | 226.461
2004-03-30 |  |  | 2005-03-30 | 23.4027 | 225.1228 | 2006-03-30 | 23.6958 | 224.8904 | 2007-03-30 | 24.5019 | 226.4707
2004-03-31 |  |  | 2005-03-31 | 23.4027 | 225.1228 | 2006-03-31 | 23.2314 | 223.8945 | 2007-03-31 | 24.4717 | 226.3822
2004-04-01 | 23.0268 | 223.5392 | 2005-04-01 | 23.2791 | 224.6074 | 2006-04-01 | 23.6007 | 224.5809 | 2007-04-01 | 24.4717 | 226.3822
2004-04-02 | 23.2302 | 223.7503 | 2005-04-02 | 23.267 | 223.9807 | 2006-04-02 | 23.7189 | 224.9069 | 2007-04-02 | 24.4913 | 226.4885
2004-04-03 | 23.2302 | 223.7503 | 2005-04-03 | 23.0379 | 223.4512 | 2006-04-03 | 23.7385 | 224.9062 | 2007-04-03 | 24.5087 | 226.4516
2004-04-04 | 22.2388 | 221.7473 | 2005-04-04 | 23.17 | 223.7785 | 2006-04-04 | 23.9203 | 225.3438 | 2007-04-04 | 24.5007 | 226.5076
2004-04-05 | 22.0566 | 221.2001 | 2005-04-05 | 23.17 | 223.7785 | 2006-04-05 | 23.6713 | 224.8296 | 2007-04-05 | 24.5006 | 226.4936
2004-04-06 | 23.2846 | 223.941 | 2005-04-06 | 22.9944 | 223.3971 | 2006-04-06 | 23.832 | 225.1114 | 2007-04-06 | 24.5042 | 226.458
2004-04-07 | 23.63 | 224.7233 | 2005-04-07 | 22.7655 | 222.9652 | 2006-04-07 | 21.0921 | 224.1262 | 2007-04-07 | 24.4333 | 226.3883
2004-04-08 | 23.6001 | 224.6315 | 2005-04-08 | 22.893 | 222.935 | 2006-04-08 | 23.5151 | 224.3207 | 2007-04-08 | 24.4463 | 226.3911
2004-04-09 | 23.634 | 224.7368 | 2005-04-09 | 22.9888 | 223.0878 | 2006-04-09 | 23.5998 | 224.8309 | 2007-04-09 | 24.4463 | 226.3911
2004-04-10 | 23.413 | 224.0547 | 2005-04-10 | 22.9674 | 223.2152 | 2006-04-10 | 23.4345 | 224.3546 | 2007-04-10
2004-04-11 | 23.1512 | 223.5898 | 2005-04-11 | 22.8379 | 222.216 | 2006-04-11 | 23.6471 | 225.5908 | 2007-04-11 | 24.5013 | 226.458
2004-04-12 | 22.2961 | 221.5108 | 2005-04-12 | 22.8379 | 222.216 | 2006-04-12 | 23.5077 | 224.1455 | 2007-04-12 | 24.5059 | 226.5287
2004-04-13 | 22.0644 | 221.2703 | 2005-04-13 | 22.9882 | 223.3114 | 2006-04-13 | 23.6062 | 224.379 | 2007-04-13 | 24.4854 | 226.4949
2004-04-14 | 22.1359 | 221.4696 | 2005-04-14 | 22.5947 | 221.1291 | 2006-04-14 | 23.5522 | 224.762 | 2007-04-14 | 24.4821 | 226.488
2004-04-15 | 22.221 | 221.6749 | 2005-04-15 | 22.5152 | 223.2557 | 2006-04-15 | 20.3391 | 222.3173 | 2007-04-15 | 24.4968 | 226.4933
2004-04-16 | 22.0323 | 221.1665 | 2005-04-16 | 18.9639 | 213.6259 | 2006-04-16 | 21.3317 | 219.1712 | 2007-04-16 | 24.499 | 226.4982
2004-04-17 | 22.0307 | 221.1177 | 2005-04-17 | 19.8404 | 214.2321 | 2006-04-17 | 19.6566 | 215.7873 | 2007-04-17 | 24.4938 | 226.4877
2004-04-18 | 22.2554 | 221.5792 | 2005-04-18 | 18.9639 | 213.6259 | 2006-04-18 | 19.5519 | 215.4071 | 2007-04-18 | 24.4974 | 226.5129
2004-04-19 | 22.2007 | 221.2222 | 2005-04-19 | 8.8576 | 154.1659 | 2006-04-19 | 14.3114 | 195.8759 | 2007-04-19 | 24.5037 | 226.4954
2004-04-20 | 23.311 | 223.807 | 2005-04-20 | 0.00080747 | 88.3062 | 2006-04-20 | 0.0011067 | 59.1855 | 2007-04-20 | 24.5011 | 226.5315
2004-04-21 | 22.9242 | 223.1901 | 2005-04-21 | 0.00074649 | 43.8747 | 2006-04-21 | 0.0013988 | 34.2446 | 2007-04-21 | 24.4993 | 226.5038
2004-04-22 | 22.9835 | 223.1415 | 2005-04-22 | 0.046136 | 32.4964 | 2006-04-22 | 0.0014668 | 32.5646 | 2007-04-22
2004-04-23 | 23.2341 | 223.906 | 2005-04-23 | 0.0020093 | 27.5732 | 2006-04-23 | 0.001481 | 33.0198 | 2007-04-23
2004-04-24 | 23.181 | 223.6593 | 2005-04-24 | 0.33634 | 102.5368 | 2006-04-24 | 0.0014621 | 32.6179 | 2007-04-24
2004-04-25 | 22.5631 | 222.3826 | 2005-04-25 | 0.40785 | 110.4408 | 2006-04-25 | 0.0014848 | 31.873 | 2007-04-25
2004-04-26 | 23.2723 | 223.6415 | 2005-04-26 | 5.4645 | 143.1781 | 2006-04-26 | 0.0010424 | 29.1923 | 2007-04-26
2004-04-27 | 23.8709 | 224.9664 | 2005-04-27 | 13.9756 | 199.8033 | 2006-04-27 |  |  | 2007-04-27
2004-04-28 | 24.2661 | 225.9331 | 2005-04-28 | 13.9975 | 199.8309 | 2006-04-28 |  |  | 2007-04-28
2004-04-29 | 24.1972 | 225.8415 | 2005-04-29 | 14.3814 | 200.9146 | 2006-04-29 | 0.68341 | 67.2492 | 2007-04-29
2004-04-30 | 23.2129 | 223.6214 | 2005-04-30 | 21.0843 | 218.5087 | 2006-04-30 | 14.4678 | 188.5231 | 2007-04-30
|  |  |  | 21.0843 | 218.5087
2004-05-01 | 21.8676 | 220.7054 | 2005-05-01 | 23.0647 | 224.0136 | 2006-05-01 | 22.392 | 221.9818 | 2007-05-01 | 24.4765 | 226.5022
2004-05-02 | 21.8574 | 220.7166 | 2005-05-02 | 22.9421 | 222.909 | 2006-05-02 | 22.2598 | 221.8069 | 2007-05-02 | 24.4962 | 226.5114
2004-05-03 | 21.851 | 220.8275 | 2005-05-03 | 23.1517 | 223.7513 | 2006-05-03 | 22.7776 | 222.9556 | 2007-05-03 | 24.002 | 225.501
2004-05-04 | 21.103 | 218.5191 | 2005-05-04 | 22.9683 | 223.0972 | 2006-05-04 | 23.5143 | 223.8487 | 2007-05-04 | 24.0106 | 225.4212
2004-05-05 | 21.103 | 218.5191 | 2005-05-05 | 22.9683 | 223.0972 | 2006-05-05 | 23.5453 | 224.5758 | 2007-05-05
2004-05-06 | 21.103 | 218.5191 | 2005-05-06 | 23.5649 | 224.6094 | 2006-05-06 | 23.2133 | 223.6989 | 2007-05-06
2004-05-07 |  |  | 2005-05-07 | 23.2577 | 223.6267 | 2006-05-07 | 21.4924 | 218.9222 | 2007-05-07
2004-05-08 |  |  | 2005-05-08 | 23.0699 | 223.5255 | 2006-05-08 | 23.1045 | 223.5883 | 2007-05-08 | 24.0128 | 225.4504
2004-05-09 |  |  | 2005-05-09 | 23.2748 | 223.8302 | 2006-05-09 | 19.6081 | 218.3982 | 2007-05-09 | 23.981 | 225.4552
2004-05-10 |  |  | 2005-05-10 | 22.3634 | 221.1192 | 2006-05-10 | 23.4545 | 224.1328 | 2007-05-10
2004-05-11 |  |  | 2005-05-11 | 23.5002 | 224.2457 | 2006-05-11 | 23.6256 | 224.5227 | 2007-05-11 | 24.2744 | 226.0684
2004-05-12 | 0 | 0 | 2005-05-12 | 23.3609 | 224.1269 | 2006-05-12 | 23.5294 | 224.0734 | 2007-05-12 | 24.0173 | 225.3133
2004-05-13 | 6.2457 | 99.2233 | 2005-05-13 | 23.3354 | 223.7562 | 2006-05-13 | 23.6312 | 223.7516 | 2007-05-13 | 23.8719 | 225.0987
2004-05-14 | -0.015713 | 33.5204 | 2005-05-14 | 23.1516 | 223.2999 | 2006-05-14 | 23.4796 | 224.438 | 2007-05-14 | 23.6191 | 224.5092
2004-05-15 | -0.016238 | 32.4624 | 2005-05-15 | 23.1516 | 223.2999 | 2006-05-15 | 23.5613 | 224.425 | 2007-05-15 | 23.8537 | 225.134
2004-05-16 | -0.016091 | 32.1336 | 2005-05-16 | 22.6598 | 224.3691 | 2006-05-16 | 23.5044 | 224.397 | 2007-05-16 | 23.8712 | 225.0516
2004-05-17 | 11.3625 | 176.3815 | 2005-05-17 | 22.2034 | 221.4417 | 2006-05-17 | 23.7358 | 224.7345 | 2007-05-17 | 23.7409 | 225.0557
2004-05-18 | 18.8819 | 213.4621 | 2005-05-18 | 22.7654 | 222.6708 | 2006-05-18 | 23.7272 | 224.9827 | 2007-05-18 | 23.781 | 225.0242
2004-05-19 | 18.2145 | 211.8561 | 2005-05-19 | 22.8281 | 221.8145 | 2006-05-19 | 23.4501 | 224.8515 | 2007-05-19 | 23.7664 | 224.9616
2004-05-20 | 21.4746 | 222.0825 | 2005-05-20 | 22.5866 | 222.3012 | 2006-05-20 | 23.5807 | 224.7027 | 2007-05-20 | 23.6579 | 225.0061
2004-05-21 | 21.4746 | 222.0825 | 2005-05-21 | 0 | 0 | 2006-05-21 | 23.2805 | 224.4573 | 2007-05-21 | 23.8648 | 225.1389
2004-05-22 | 21.9925 | 221.8707 | 2005-05-22 | 0 | 0 | 2006-05-22 | 23.4358 | 224.1643 | 2007-05-22 | 23.6696 | 224.8739
2004-05-23 | 22.9978 | 223.2646 | 2005-05-23 | 0 | 0 | 2006-05-23 | 23.6407 | 224.5026 | 2007-05-23 | 23.5883 | 224.7236
2004-05-24 | 23.0039 | 223.2372 | 2005-05-24 |  |  | 2006-05-24 | 23.6822 | 224.6058 | 2007-05-24 | 23.6088 | 224.4354
2004-05-25 | 23.3182 | 223.9502 | 2005-05-25 |  |  | 2006-05-25 | 23.3189 | 223.673 | 2007-05-25 | 23.511 | 223.7958
2004-05-26 | 23.2782 | 223.8892 | 2005-05-26 | 22.9963 | 223.0916 | 2006-05-26 | 23.1651 | 223.6438 | 2007-05-26 | 23.6124 | 224.6162
2004-05-27 | 23.1483 | 223.6567 | 2005-05-27 | 22.8543 | 222.8826 | 2006-05-27 | 23.5698 | 224.5356 | 2007-05-27 | 23.7961 | 224.9463
2004-05-28 | 23.4464 | 223.8696 | 2005-05-28 | 22.8209 | 222.6451 | 2006-05-28 | 23.999 | 225.061 | 2007-05-28 | 20.7306 | 215.9117
2004-05-29 | 23.5943 | 224.4937 | 2005-05-29 | 23.3 | 222.9673 | 2006-05-29 | 23.4527 | 224.3858 | 2007-05-29 | 12.6229 | 186.025
2004-05-30 | 23.4384 | 223.8431 | 2005-05-30 | 23.3 | 222.9673 | 2006-05-30 | 23.5943 | 224.6277 | 2007-05-30 | 10.7916 | 182.4041
2004-05-31 | 23.4384 | 223.8431 | 2005-05-31 | 23.3 | 222.9673 | 2006-05-31 | 23.6169 | 223.9609 | 2007-05-31 | 4.6008 | 130.872
2004-06-01 | 24.1897 | 225.9389 | 2005-06-01 | 22.8157 | 222.7816 | 2006-06-01 | 23.4877 | 224.068 | 2007-06-01
2004-06-02 | 24.1326 | 225.6566 | 2005-06-02 | 22.8299 | 222.6196 | 2006-06-02 | 23.0618 | 223.3538 | 2007-06-02
2004-06-03 | 23.9259 | 225.2712 | 2005-06-03 | 22.7052 | 222.1253 | 2006-06-03 | 23.0746 | 223.4144 | 2007-06-03
2004-06-04 | 23.4098 | 222.4294 | 2005-06-04 | 22.8309 | 222.921 | 2006-06-04 | 23.5956 | 224.571 | 2007-06-04
2004-06-05 | 23.4098 | 222.4294 | 2005-06-05 | 22.8309 | 222.921 | 2006-06-05 | 23.4085 | 224.1142 | 2007-06-05
2004-06-06 | 23.9942 | 224.8528 | 2005-06-06 | 22.2274 | 221.3443 | 2006-06-06 | 23.5071 | 224.364 | 2007-06-06
2004-06-07 | 23.9457 | 225.2953 | 2005-06-07 | 22.6157 | 222.2913 | 2006-06-07 | 23.4906 | 224.2877 | 2007-06-07
2004-06-08 | 23.943 | 225.219 | 2005-06-08 | 22.8959 | 222.7872 | 2006-06-08 | 23.9349 | 225.2808 | 2007-06-08
2004-06-09 | 23.9762 | 225.238 | 2005-06-09 | 22.8673 | 224.0634 | 2006-06-09 | 23.623 | 224.6605 | 2007-06-09
2004-06-10 | 23.9576 | 225.1411 | 2005-06-10 | 22.0912 | 221.1149 | 2006-06-10 | 23.6364 | 224.6702 | 2007-06-10
2004-06-11 | 23.9543 | 225.1966 | 2005-06-11 | 22.8186 | 224.0739 | 2006-06-11 | 23.3742 | 224.2388 | 2007-06-11 | 23.795 | 224.4385
2004-06-12 | 23.9422 | 225.2365 | 2005-06-12 | 22.5487 | 224.1516 | 2006-06-12 | 23.7077 | 224.805 | 2007-06-12
2004-06-13 | 23.9545 | 225.1574 | 2005-06-13 | 22.6652 | 223.4985 | 2006-06-13 | 23.4941 | 224.304 | 2007-06-13 | 24.0043 | 225.2749
2004-06-14 | 23.8161 | 224.6941 | 2005-06-14 | 22.6509 | 222.0652 | 2006-06-14 | 23.6675 | 225.1691 | 2007-06-14 | 24.0124 | 225.3896
2004-06-15 | 23.3729 | 223.9779 | 2005-06-15 | 22.7849 | 222.5815 | 2006-06-15 | 23.1434 | 223.4116 | 2007-06-15 | 23.9633 | 225.28
2004-06-16 | 23.1153 | 223.4141 | 2005-06-16 | 22.5843 | 222.1609 | 2006-06-16 | 23.5885 | 224.5845 | 2007-06-16 | 23.7584 | 224.8131
2004-06-17 | 23.2188 | 223.6623 | 2005-06-17 | 22.8403 | 222.9083 | 2006-06-17 | 23.7688 | 224.8327 | 2007-06-17
2004-06-18 | 23.6325 | 224.5659 | 2005-06-18 | 23.1584 | 223.6646 | 2006-06-18 | 22.2405 | 218.9954 | 2007-06-18 | 23.894 | 225.0981
2004-06-19 | 23.731 | 224.7108 | 2005-06-19 | 23.2123 | 223.777 | 2006-06-19 | 23.2274 | 223.9141 | 2007-06-19 | 24.1324 | 225.6065
2004-06-20 | 23.9259 | 225.0738 | 2005-06-20 | 22.8687 | 223.2775 | 2006-06-20 | 23.8589 | 224.9855 | 2007-06-20
2004-06-21 | 23.9954 | 225.3248 | 2005-06-21 | 22.8165 | 222.9309 | 2006-06-21 | 23.6353 | 224.4802 | 2007-06-21
2004-06-22 | 23.5835 | 224.4016 | 2005-06-22 | 23.0898 | 223.0848 | 2006-06-22 | 23.2423 | 223.762 | 2007-06-22
2004-06-23 | 23.6684 | 224.557 | 2005-06-23 | 22.8171 | 223.0385 | 2006-06-23 | 23.7714 | 224.7241 | 2007-06-23 | 23.9855 | 225.3929
2004-06-24 | 23.6069 | 224.4059 | 2005-06-24 | 23.1317 | 223.5474 | 2006-06-24 | 23.2979 | 224.0206 | 2007-06-24 | 23.9173 | 225.0801
2004-06-25 | 23.2446 | 223.657 | 2005-06-25 | 22.9326 | 223.8991 | 2006-06-25 | 23.6059 | 224.3528 | 2007-06-25 | 23.9493 | 225.1895
2004-06-26 | 23.2723 | 223.6415 | 2005-06-26 | 22.8513 | 223.0583 | 2006-06-26 | 23.5732 | 224.5224 | 2007-06-26 | 23.8359 | 225.1747
2004-06-27 | 23.321 | 223.8025 | 2005-06-27 | 22.3761 | 221.8559 | 2006-06-27 | 23.3021 | 223.7513 | 2007-06-27 | 23.8003 | 224.6961
2004-06-28 | 23.321 | 223.8025 | 2005-06-28 | 23.0104 | 223.3955 | 2006-06-28 | 23.408 | 223.9232 | 2007-06-28 | 24.0768 | 225.4776
2004-06-29 | 23.7427 | 224.7175 | 2005-06-29 | 23.3417 | 224.1356 | 2006-06-29 | 23.6861 | 224.4489 | 2007-06-29 | 23.9981 | 225.4178
2004-06-30 | 24.0145 | 225.28 | 2005-06-30 | 23.4027 | 225.1228 | 2006-06-30 | 23.7853 | 224.7877 | 2007-06-30 | 23.9305 | 225.2327
2004-07-01 | 23.6873 | 224.6117 | 2005-07-01 | 23.1516 | 223.2999 | 2006-07-01 | 23.4454 | 223.9395 | 2007-07-01 | 23.8827 | 225.2808
2004-07-02 | 23.041 | 223.2984 | 2005-07-02 | 22.6598 | 224.3691 | 2006-07-02 | 23.4612 | 224.0435 | 2007-07-02 | 23.9048 | 225.1831
2004-07-03 | 23.1188 | 223.5153 | 2005-07-03 | 22.2034 | 221.4417 | 2006-07-03 | 23.1943 | 223.5041 | 2007-07-03 | 23.9124 | 225.2505
2004-07-04 | 23.5972 | 224.4647 | 2005-07-04 | 22.7654 | 222.6708 | 2006-07-04 | 23.3557 | 223.6649 | 2007-07-04 | 23.9752 | 225.3502
2004-07-05 | 23.5972 | 224.4647 | 2005-07-05 | 22.8281 | 221.8145 | 2006-07-05 | 23.1979 | 223.6125 | 2007-07-05 | 23.9532 | 225.2978
2004-07-06 | 23.4942 | 224.0733 | 2005-07-06 | 22.5866 | 222.3012 | 2006-07-06 | 23.989 | 224.2203 | 2007-07-06 | 23.8038 | 224.9163
2004-07-07 | 23.0803 | 223.2928 | 2005-07-07 | 24.2331 | 226.0803 | 2006-07-07 | 23.3784 | 223.4754 | 2007-07-07 | 24.1066 | 225.646
2004-07-08 | 23.104 | 223.3292 | 2005-07-08 | 22.9047 | 223.1382 | 2006-07-08 | 22.7161 | 222.4622 | 2007-07-08 | 23.9752 | 225.1923
2004-07-09 | 22.3163 | 220.223 | 2005-07-09 | 23.3389 | 224.0677 | 2006-07-09 | 23.2001 | 223.6496 | 2007-07-09 | 24.0956 | 225.8782
2004-07-10 | 22.2858 | 219.8364 | 2005-07-10 | 23.168 | 223.6852 | 2006-07-10 | 23.518 | 224.1509 | 2007-07-10
2004-07-11 | 22.202 | 221.6187 | 2005-07-11 | 23.0009 | 223.469 | 2006-07-11 | 23.7551 | 224.7793 | 2007-07-11 | 23.8047 | 224.8126
2004-07-12 | 22.6328 | 222.1698 | 2005-07-12 | 23.5876 | 224.4136 | 2006-07-12 | 23.3871 | 223.8963 | 2007-07-12 | 23.8042 | 225.0816
2004-07-13 | 22.1903 | 221.3137 | 2005-07-13 | 22.0045 | 220.7296 | 2006-07-13 | 23.6642 | 224.9039 | 2007-07-13 | 24.142 | 225.3367
2004-07-14 | 21.8165 | 220.3494 | 2005-07-14 | 21.9583 | 220.7256 | 2006-07-14 | 23.7086 | 224.457 | 2007-07-14 | 23.7684 | 224.7892
2004-07-15 | 21.6893 | 220.1691 | 2005-07-15 | 24.0596 | 225.2831 | 2006-07-15 | 23.6475 | 224.4072 | 2007-07-15 | 23.7449 | 224.778
2004-07-16 | 21.009 | 218.7658 | 2005-07-16 | 22.9344 | 223.2727 | 2006-07-16 | 23.6244 | 224.589 | 2007-07-16 | 23.8969 | 224.7531
2004-07-17 | 20.779 | 218.0682 | 2005-07-17 | 22.8157 | 222.7816 | 2006-07-17 | 23.4547 | 224.0219 | 2007-07-17 | 23.7606 | 224.7027
2004-07-18 | 21.3827 | 219.5496 | 2005-07-18 | 22.8299 | 222.6196 | 2006-07-18 | 23.5191 | 224.6341 | 2007-07-18 | 23.9242 | 225.4092
2004-07-19 | 21.7308 | 220.3133 | 2005-07-19 | 22.7052 | 222.1253 | 2006-07-19 | 23.7233 | 224.5077 | 2007-07-19 | 23.9918 | 225.2658
2004-07-20 | 21.9454 | 220.6418 | 2005-07-20 | 22.8309 | 222.921 | 2006-07-20 | 23.832 | 224.7894 | 2007-07-20 | 23.9988 | 225.2706
2004-07-21 | 22.0578 | 221.0373 | 2005-07-21 | 22.8309 | 222.921 | 2006-07-21 | 23.6411 | 224.5934 | 2007-07-21 | 24.0197 | 225.3207
2004-07-22 | 22.0026 | 220.8824 | 2005-07-22 | 22.2274 | 221.3443 | 2006-07-22 | 23.3523 | 223.9993 | 2007-07-22 | 24.0104 | 225.3105
2004-07-23 | 21.9264 | 220.723 | 2005-07-23 | 22.6157 | 222.2913 | 2006-07-23 | 23.3294 | 223.4757 | 2007-07-23 | 24 | 225.3286
2004-07-24 | 22.1708 | 221.1596 | 2005-07-24 | 22.8959 | 222.7872 | 2006-07-24 |  |  | 2007-07-24 | 24.0349 | 225.5231
2004-07-25 | 22.5114 | 222.0179 | 2005-07-25 | 22.8673 | 224.0634 | 2006-07-25 | 23.0056 | 223.2006 | 2007-07-25 | 24.0147 | 225.5837
2004-07-26 | 22.4339 | 221.7809 | 2005-07-26 | 22.0912 | 221.1149 | 2006-07-26 | 23.4703 | 224.1636 | 2007-07-26 | 23.3267 | 223.7488
2004-07-27 | 21.7591 | 221.2072 | 2005-07-27 | 22.8379 | 222.216 | 2006-07-27 | 23.4318 | 223.9395 | 2007-07-27 | 23.8934 | 224.9687
2004-07-28 | 19.2602 | 219.2042 | 2005-07-28 | 22.9882 | 223.3114 | 2006-07-28 | 23.0938 | 223.5433 | 2007-07-28 | 23.7987 | 225.6147
2004-07-29 | 21.4311 | 219.6887 | 2005-07-29 | 22.5947 | 221.1291 | 2006-07-29 | 23.4051 | 223.9708 | 2007-07-29 | 24.4638 | 226.2024
2004-07-30 | 21.8764 | 220.0384 | 2005-07-30 | 23.4027 | 225.1228 | 2006-07-30 | 23.2699 | 223.2582 | 2007-07-30 | 23.917 | 225.2042
2004-07-31 | 23.1137 | 223.311 | 2005-07-31 | 23.4027 | 225.1228 | 2006-07-31 | 23.5366 | 224.2358 | 2007-07-31 | 23.765 | 224.8062
2004-08-01 | 22.9422 | 222.8455 | 2005-08-01 | 24.2331 | 226.0803 | 2006-08-01 |  |  | 2007-08-01 | 23.9374 | 224.9242
2004-08-02 | 23.3373 | 223.9993 | 2005-08-02 | 22.9047 | 223.1382 | 2006-08-02 |  |  | 2007-08-02 | 23.5545 | 224.4075
2004-08-03 | 23.453 | 223.9733 | 2005-08-03 | 23.3389 | 224.0677 | 2006-08-03 | 23.2158 | 223.5914 | 2007-08-03 | 23.8476 | 224.8589
2004-08-04 | 22.4313 | 221.1464 | 2005-08-04 | 23.168 | 223.6852 | 2006-08-04 | 23.4468 | 223.9227 | 2007-08-04 | 23.7722 | 224.7167
2004-08-05 | 22.4313 | 221.1464 | 2005-08-05 | 23.0009 | 223.469 | 2006-08-05 | 23.1644 | 223.4535 | 2007-08-05 | 23.6422 | 224.4743
2004-08-06 | 21.5865 | 219.828 | 2005-08-06 | 22.8157 | 222.7816 | 2006-08-06 | 23.1416 | 223.5673 | 2007-08-06 | 23.5814 | 224.2427
2004-08-07 | 22.8379 | 222.6942 | 2005-08-07 | 22.8299 | 222.6196 | 2006-08-07 | 23.3207 | 223.6127 | 2007-08-07 | 23.5332 | 224.4049
2004-08-08 | 22.3919 | 221.6451 | 2005-08-08 | 22.7052 | 222.1253 | 2006-08-08 | 23.4487 | 224.9873 | 2007-08-08 | 23.59 | 224.3556
2004-08-09 | 22.5916 | 221.8992 | 2005-08-09 | 22.8309 | 222.921 | 2006-08-09 |  |  | 2007-08-09
2004-08-10 | 19.8401 | 214.7233 | 2005-08-10 | 22.8309 | 222.921 | 2006-08-10 | 23.6006 | 223.3329 | 2007-08-10
2004-08-11 | 0 | 224.6943 | 2005-08-11 | 22.2274 | 221.3443 | 2006-08-11 |  |  | 2007-08-11
2004-08-12 | 23.9079 | 225.0934 | 2005-08-12 | 22.6157 | 222.2913 | 2006-08-12 | 23.1981 | 223.449 | 2007-08-12
2004-08-13 |  |  | 2005-08-13 | 22.8959 | 222.7872 | 2006-08-13 |  |  | 2007-08-13
2004-08-14 |  |  | 2005-08-14 | 22.8673 | 224.0634 | 2006-08-14 | 23.4269 | 223.9363 | 2007-08-14
2004-08-15 |  |  | 2005-08-15 | 22.0912 | 221.1149 | 2006-08-15 | 23.1569 | 223.4184 | 2007-08-15
2004-08-16 | 23.9079 | 225.0934 | 2005-08-16 | 23.1516 | 223.2999 | 2006-08-16 | 23.2017 | 223.6038 | 2007-08-16
2004-08-17 | 21.7319 | 220.2148 | 2005-08-17 | 22.6598 | 224.3691 | 2006-08-17 | 23.3492 | 223.8546 | 2007-08-17
2004-08-18 | 22.971 | 222.8882 | 2005-08-18 | 22.2034 | 221.4417 | 2006-08-18 | 23.1405 | 223.2117 | 2007-08-18
2004-08-19 |  |  | 2005-08-19 | 22.7654 | 222.6708 | 2006-08-19 | 23.1006 | 223.0876 | 2007-08-19
2004-08-20 | 21.4948 | 219.5801 | 2005-08-20 | 22.8281 | 221.8145 | 2006-08-20 | 23.1814 | 223.2096 | 2007-08-20
2004-08-21 | 23.5368 | 224.1516 | 2005-08-21 | 22.5866 | 222.3012 | 2006-08-21 | 23.1372 | 223.3406 | 2007-08-21
2004-08-22 | 23.0589 | 223.114 | 2005-08-22 | 24.2331 | 226.0803 | 2006-08-22 | 23.2755 | 223.1997 | 2007-08-22
2004-08-23 | 22.3384 | 221.5698 | 2005-08-23 | 22.9047 | 223.1382 | 2006-08-23 | 23.2452 | 223.1334 | 2007-08-23
2004-08-24 | 22.338 | 221.6004 | 2005-08-24 | 23.3389 | 224.0677 | 2006-08-24 | 23.0982 | 223.4927 | 2007-08-24
2004-08-25 | 21.2434 | 219.0552 | 2005-08-25 | 23.168 | 223.6852 | 2006-08-25 | 23.1101 | 223.4998 | 2007-08-25
2004-08-26 | 22.6891 | 222.3633 | 2005-08-26 | 23.0009 | 223.469 | 2006-08-26 | 23.118 | 223.2262 | 2007-08-26
2004-08-27 | 19.0723 | 213.8428 | 2005-08-27 |  |  | 2006-08-27 | 22.9426 | 222.9541 | 2007-08-27
2004-08-28 | 19.3103 | 214.3677 | 2005-08-28 |  |  | 2006-08-28 | 22.9411 | 222.7918 | 2007-08-28
2004-08-29 | 21.3492 | 219.3115 | 2005-08-29 |  |  | 2006-08-29 | 22.9411 | 222.1497 | 2007-08-29
2004-08-30 | 14.276 | 200.3357 | 2005-08-30 |  |  | 2006-08-30 | 20.2901 | 216.0763 | 2007-08-30
2004-08-31 | 13.7595 | 198.7885 | 2005-08-31 |  |  | 2006-08-31 | 20.8215 | 217.4872 | 2007-08-31
2004-09-01 | 15.1057 | 202.8564 | 2005-09-01 | 22.9344 | 223.2727 | 2006-09-01 | 14.5817 | 189.9132 | 2007-09-01
2004-09-02 | 14.8572 | 202.0996 | 2005-09-02 |  |  | 2006-09-02 |  |  | 2007-09-02
2004-09-03 | 15.125 | 202.8382 | 2005-09-03 |  |  | 2006-09-03 |  |  | 2007-09-03
2004-09-04 | 14.6228 | 201.471 | 2005-09-04 |  |  | 2006-09-04 |  |  | 2007-09-04
2004-09-05 | 14.6228 | 201.471 | 2005-09-05 |  |  | 2006-09-05 |  |  | 2007-09-05
2004-09-06 | 20.4863 | 217.2913 | 2005-09-06 |  |  | 2006-09-06 |  |  | 2007-09-06
2004-09-07 | 21.1693 | 218.9148 | 2005-09-07 | 22.8157 | 222.7816 | 2006-09-07 |  |  | 2007-09-07
2004-09-08 | 24.4258 | 226.0437 | 2005-09-08 | 22.8299 | 222.6196 | 2006-09-08 |  |  | 2007-09-08
2004-09-09 | 22.9326 | 222.876 | 2005-09-09 | 22.7052 | 222.1253 | 2006-09-09 | 17.3648 | 206.0668 | 2007-09-09
2004-09-10 | 20.6987 | 217.7856 | 2005-09-10 | 22.8309 | 222.921 | 2006-09-10 | 21.4019 | 219.3998 | 2007-09-10
2004-09-11 | 20.9148 | 218.2923 | 2005-09-11 | 22.8309 | 222.921 | 2006-09-11 | 22.5334 | 222.1006 | 2007-09-11
2004-09-12 | 21.416 | 219.4519 | 2005-09-12 | 22.2274 | 221.3443 | 2006-09-12 | 22.5733 | 222.0119 | 2007-09-12
2004-09-13 | 21.5213 | 219.6777 | 2005-09-13 | 22.6157 | 222.2913 | 2006-09-13 | 23.3439 | 223.4207 | 2007-09-13
2004-09-14 | 20.7385 | 217.9138 | 2005-09-14 | 22.8959 | 222.7872 | 2006-09-14 | 23.8497 | 224.7495 | 2007-09-14
2004-09-15 | 21.9466 | 220.5994 | 2005-09-15 | 22.8673 | 224.0634 | 2006-09-15 | 24.0377 | 225.3471 | 2007-09-15
2004-09-16 | 21.3309 | 219.1834 | 2005-09-16 | 22.0912 | 221.1149 | 2006-09-16 | 23.6636 | 224.7582 | 2007-09-16
2004-09-17 | 23.703 | 224.53 | 2005-09-17 |  |  | 2006-09-17 | 23.7764 | 224.7978 | 2007-09-17
2004-09-18 | 24.131 | 225.409 | 2005-09-18 |  |  | 2006-09-18 | 23.8596 | 223.6168 | 2007-09-18
2004-09-19 | 23.7053 | 224.5483 | 2005-09-19 |  |  | 2006-09-19 | 23.1908 | 223.6272 | 2007-09-19
2004-09-20 | 22.5664 | 222.0947 | 2005-09-20 |  |  | 2006-09-20 | 23.6341 | 224.3248 | 2007-09-20
2004-09-21 | 21.5085 | 219.5801 | 2005-09-21 |  |  | 2006-09-21 | 23.2578 | 223.8927 | 2007-09-21
2004-09-22 | 21.8362 | 220.4529 | 2005-09-22 |  |  | 2006-09-22 | 23.4357 | 224.0224 | 2007-09-22
2004-09-23 | 23.0397 | 223.1323 | 2005-09-23 |  |  | 2006-09-23 | 23.2412 | 223.4594 | 2007-09-23
2004-09-24 | 24.0074 | 225.1831 | 2005-09-24 |  |  | 2006-09-24 | 23.6447 | 225.2991 | 2007-09-24
2004-09-25 | 21.5126 | 219.6899 | 2005-09-25 |  |  | 2006-09-25 | 23.2408 | 224.4754 | 2007-09-25
2004-09-26 | 20.647 | 217.6697 | 2005-09-26 |  |  | 2006-09-26 | 23.6184 | 224.586 | 2007-09-26
2004-09-27 | 6.0929 | 166.9251 | 2005-09-27 |  |  | 2006-09-27 | 23.722 | 224.588 | 2007-09-27
2004-09-28 | 7.0361 | 171.9422 | 2005-09-28 |  |  | 2006-09-28 | 23.5598 | 224.2472 | 2007-09-28
2004-09-29 | 7.2388 | 173.053 | 2005-09-29 |  |  | 2006-09-29 | 23.635 | 224.3281 | 2007-09-29
2004-09-30 | 7.0483 | 172.052 | 2005-09-30 |  |  | 2006-09-30 | 23.9289 | 224.9433 | 2007-09-30
2004-10-01 | 7.2283 | 172.9431 | 2005-10-01 | 24.2331 | 226.0803 | 2006-10-01 | 23.6966 | 224.1147 | 2007-10-01 | 23.8186 | 224.865
2004-10-02 | 13.328 | 197.403 | 2005-10-02 | 22.9047 | 223.1382 | 2006-10-02 | 23.5718 | 224.0939 | 2007-10-02 | 23.941 | 225.0346
2004-10-03 | 6.7497 | 170.4102 | 2005-10-03 | 23.3389 | 224.0677 | 2006-10-03 | 23.2767 | 223.3101 | 2007-10-03 | 23.9749 | 225.1122
2004-10-04 | 17.5259 | 209.8206 | 2005-10-04 | 23.168 | 223.6852 | 2006-10-04 | 23.169 | 223.3261 | 2007-10-04 | 23.9447 | 225.1305
2004-10-05 | 17.5259 | 209.8206 | 2005-10-05 | 23.0009 | 223.469 | 2006-10-05 | 23.4477 | 224.4247 | 2007-10-05 | 23.8914 | 224.7999
2004-10-06 | 23.947 | 225.1831 | 2005-10-06 | 22.8379 | 222.216 | 2006-10-06 | 23.1691 | 223.5095 | 2007-10-06 | 24.0653 | 225.2909
2004-10-07 |  |  | 2005-10-07 | 22.9882 | 223.3114 | 2006-10-07 | 23.0559 | 222.9836 | 2007-10-07 | 23.8803 | 225.2096
2004-10-08 | 23.2365 | 223.6389 | 2005-10-08 | 22.5947 | 221.1291 | 2006-10-08 | 23.1831 | 223.6018 | 2007-10-08 | 23.7593 | 224.9112
2004-10-09 | 23.2365 | 223.6389 | 2005-10-09 | 23.4027 | 225.1228 | 2006-10-09 | 22.6448 | 222.0741 | 2007-10-09 | 23.9219 | 224.5923
2004-10-10 | 23.3995 | 223.877 | 2005-10-10 | 23.4027 | 225.1228 | 2006-10-10 | 23.372 | 223.8714 | 2007-10-10
2004-10-11 | 23.8486 | 224.9146 | 2005-10-11 | 22.8157 | 222.7816 | 2006-10-11 | 23.3792 | 223.5939 | 2007-10-11
2004-10-12 | 24.0523 | 225.2991 | 2005-10-12 | 22.8299 | 222.6196 | 2006-10-12 | 23.4232 | 223.8673 | 2007-10-12 | 24.1203 | 225.779
2004-10-13 | 22.6245 | 222.2412 | 2005-10-13 | 22.7052 | 222.1253 | 2006-10-13 | 23.4051 | 223.8345 | 2007-10-13 | 23.8758 | 225.0354
2004-10-14 | 23.0022 | 223.1323 | 2005-10-14 | 22.8309 | 222.921 | 2006-10-14 | 23.5893 | 224.2948 | 2007-10-14 | 23.9373 | 225.1132
2004-10-15 | 22.9166 | 222.8577 | 2005-10-15 | 22.8309 | 222.921 | 2006-10-15 | 23.5491 | 224.6892 | 2007-10-15 | 23.8683 | 225.0079
2004-10-16 | 22.836 | 222.7295 | 2005-10-16 | 22.2274 | 221.3443 | 2006-10-16 | 23.4631 | 223.9245 | 2007-10-16 | 23.8469 | 224.9191
2004-10-17 | 24.0331 | 225.2991 | 2005-10-17 | 22.6157 | 222.2913 | 2006-10-17 | 23.5094 | 224.5888 | 2007-10-17 | 23.932 | 225.2352
2004-10-18 | 23.6321 | 224.3896 | 2005-10-18 | 22.8959 | 222.7872 | 2006-10-18 | 23.0649 | 223.1337 | 2007-10-18 | 23.9399 | 225.3405
2004-10-19 | 22.2725 | 221.3623 | 2005-10-19 | 22.8673 | 224.0634 | 2006-10-19 | 23.1433 | 223.3452 | 2007-10-19 | 24.084 | 225.4776
2004-10-20 | 24.1887 | 225.5371 | 2005-10-20 | 22.0912 | 221.1149 | 2006-10-20 | 23.3613 | 0 | 2007-10-20 | 23.7118 | 224.9535
2004-10-21 | 23.7145 | 224.5941 | 2005-10-21 | 23.1516 | 223.2999 | 2006-10-21 | 23.1913 | 223.4609 | 2007-10-21 | 23.8481 | 224.943
2004-10-22 | 23.9288 | 225.0394 | 2005-10-22 | 22.6598 | 224.3691 | 2006-10-22 | 22.8697 | 222.6097 | 2007-10-22 | 23.9401 | 225.2553
2004-10-23 | 23.9009 | 225.042 | 2005-10-23 | 22.2034 | 221.4417 | 2006-10-23 | 22.7148 | 222.4838 | 2007-10-23 | 23.8232 | 224.9629
2004-10-24 | 23.8777 | 224.7009 | 2005-10-24 | 22.7654 | 222.6708 | 2006-10-24 | 23.0031 | 223.5715 | 2007-10-24 | 23.9025 | 225.0951
2004-10-25 | 23.934 | 225.1107 | 2005-10-25 | 22.8281 | 221.8145 | 2006-10-25 | 23.1984 | 223.3279 | 2007-10-25 | 23.5137 | 224.2065
2004-10-26 | 23.9851 | 225.1778 | 2005-10-26 | 22.5866 | 222.3012 | 2006-10-26 | 22.9342 | 222.8533 | 2007-10-26 | 23.7387 | 224.8547
2004-10-27 | 23.9094 | 225.0298 | 2005-10-27 | 23.5876 | 224.4136 | 2006-10-27 | 23.0437 | 223.4469 | 2007-10-27 | 23.9202 | 225.2256
2004-10-28 | 23.8959 | 225.0725 | 2005-10-28 | 22.0045 | 220.7296 | 2006-10-28 | 23.1943 | 223.4807 | 2007-10-28 | 23.9107 | 225.0379
2004-10-29 | 23.9829 | 225.2268 | 2005-10-29 | 21.9583 | 220.7256 | 2006-10-29 | 23.09 | 223.2081 | 2007-10-29 | 24.1611 | 225.6521
2004-10-30 | 23.2979 | 224.2193 | 2005-10-30 | 24.0596 | 225.2831 | 2006-10-30 | 23.3123 | 223.8709 | 2007-10-30 | 23.9315 | 225.3718
2004-10-31 | 23.2863 | 222.8055 | 2005-10-31 |  |  | 2006-10-31 | 23.065 | 223.1921 | 2007-10-31 | 24.2037 | 226.0994
2004-11-01 | 23.7091 | 223.9815 | 2005-11-01 | 23.1516 | 223.2999 | 2006-11-01 | 22.895 | 222.7079 | 2007-11-01 | 23.8676 | 224.1946
2004-11-02 | 21.4534 | 223.554 | 2005-11-02 | 22.6598 | 224.3691 | 2006-11-02 | 23.4127 | 223.7999 | 2007-11-02 | 23.9619 | 225.9717
2004-11-03 | 21.5753 | 219.5719 | 2005-11-03 | 22.2034 | 221.4417 | 2006-11-03 | 23.7164 | 224.6022 | 2007-11-03 | 24.0545 | 225.6958
2004-11-04 | 23.2638 | 222.9914 | 2005-11-04 | 22.7654 | 222.6708 | 2006-11-04 | 23.3623 | 223.6577 | 2007-11-04 | 23.8565 | 224.8169
2004-11-05 | 23.2638 | 222.9914 | 2005-11-05 | 22.8281 | 221.8145 | 2006-11-05 | 23.4869 | 224.5227 | 2007-11-05 | 23.8909 | 224.1638
2004-11-06 | 23.0912 | 223.4347 | 2005-11-06 | 22.5866 | 222.3012 | 2006-11-06 | 23.3934 | 223.9634 | 2007-11-06 | 24.8715 | 226.4282
2004-11-07 | 23.4133 | 222.2827 | 2005-11-07 | 24.2331 | 226.0803 | 2006-11-07 | 23.2854 | 223.7506 | 2007-11-07 | 23.8232 | 225.2057
2004-11-08 | 22.8796 | 222.997 | 2005-11-08 | 22.9047 | 223.1382 | 2006-11-08 | 23.504 | 224.7063 | 2007-11-08 | 23.6733 | 224.9451
2004-11-09 | 22.9374 | 222.7547 | 2005-11-09 | 23.3389 | 224.0677 | 2006-11-09 | 22.6429 | 222.2936 | 2007-11-09 | 23.727 | 225.0982
2004-11-10 | 23.8834 | 225.1709 | 2005-11-10 | 23.168 | 223.6852 | 2006-11-10 | 23.7372 | 224.882 | 2007-11-10
2004-11-11 |  |  | 2005-11-11 | 23.0009 | 223.469 | 2006-11-11 | 23.4496 | 224.2681 | 2007-11-11 | 24.0375 | 225.5348
2004-11-12 |  |  | 2005-11-12 | 23.5876 | 224.4136 | 2006-11-12 | 23.145 | 223.8436 | 2007-11-12 | 23.9446 | 225.4824
2004-11-13 |  |  | 2005-11-13 | 22.0045 | 220.7296 | 2006-11-13 | 23.3559 | 223.9563 | 2007-11-13 | 23.8235 | 225.1508
2004-11-14 |  |  | 2005-11-14 | 21.9583 | 220.7256 | 2006-11-14 | 23.1677 | 222.9856 | 2007-11-14 | 23.7758 | 224.3518
2004-11-15 |  |  | 2005-11-15 | 24.0596 | 225.2831 | 2006-11-15 | 23.2759 | 223.3632 | 2007-11-15 | 23.6758 | 224.6018
2004-11-16 |  |  | 2005-11-16 |  |  | 2006-11-16 | 23.6632 | 224.4975 | 2007-11-16 | 23.4575 | 224.5723
2004-11-17 | 23.2202 | 223.623 | 2005-11-17 |  |  | 2006-11-17 | 23.5156 | 224.8304 | 2007-11-17 | 23.6469 | 224.6836
2004-11-18 | 23.3049 | 223.0871 | 2005-11-18 |  |  | 2006-11-18 | 23.4212 | 224.3721 | 2007-11-18 | 23.7576 | 225.2269
2004-11-19 | 23.275 | 223.9075 | 2005-11-19 | 24.2331 | 226.0803 | 2006-11-19 | 22.9987 | 223.2422 | 2007-11-19 | 23.7193 | 225.0432
2004-11-20 | 23.182 | 224.0356 | 2005-11-20 | 22.9047 | 223.1382 | 2006-11-20 | 23.3392 | 223.1178 | 2007-11-20 | 23.9063 | 225.266
2004-11-21 | 23.4988 | 224.2846 | 2005-11-21 | 23.3389 | 224.0677 | 2006-11-21 | 24.3973 | 223.5814 | 2007-11-21 | 20.5483 | 217.1811
2004-11-22 | 23.2612 | 223.7783 | 2005-11-22 | 23.168 | 223.6852 | 2006-11-22 | 23.4793 | 224.1964 | 2007-11-22
2004-11-23 | 23.2542 | 223.7173 | 2005-11-23 | 23.0009 | 223.469 | 2006-11-23 | 23.2836 | 223.674 | 2007-11-23
2004-11-24 | 22.8079 | 222.8686 | 2005-11-24 |  |  | 2006-11-24 | 23.3513 | 223.7498 | 2007-11-24
2004-11-25 | 22.8818 | 223.0153 | 2005-11-25 |  |  | 2006-11-25 | 23.729 | 224.6872 | 2007-11-25
2004-11-26 | 23.7013 | 224.8879 | 2005-11-26 |  |  | 2006-11-26 | 23.4317 | 224.3418 | 2007-11-26
2004-11-27 | 21.6564 | 219.5842 | 2005-11-27 |  |  | 2006-11-27 | 23.4292 | 224.0835 | 2007-11-27
2004-11-28 | 22.6979 | 222.6084 | 2005-11-28 | 22.8379 | 222.216 | 2006-11-28 | 23.4649 | 224.1765 | 2007-11-28
2004-11-29 | 23.1997 | 223.7017 | 2005-11-29 | 22.9882 | 223.3114 | 2006-11-29 | 23.5509 | 224.4011 | 2007-11-29
2004-11-30 | 22.8759 | 223.0036 | 2005-11-30 | 22.5947 | 221.1291 | 2006-11-30 | 24.3155 | 225.985 | 2007-11-30
2004-12-01 | 22.8053 | 222.85 | 2005-12-01 |  |  | 2006-12-01 | 23.4817 | 224.2363 | 2007-12-01
2004-12-02 | 23.3116 | 224.1242 | 2005-12-02 |  |  | 2006-12-02 | 22.0976 | 223.9403 | 2007-12-02
2004-12-03 | 22.5058 | 222.2893 | 2005-12-03 |  |  | 2006-12-03 | 23.9406 | 224.6386 | 2007-12-03 | 23.9819 | 225.459
2004-12-04 | 23.052 | 223.2463 | 2005-12-04 |  |  | 2006-12-04 | 23.5724 | 224.705 | 2007-12-04 | 23.9939 | 225.5211
2004-12-05 | 23.052 | 223.2463 | 2005-12-05 |  |  | 2006-12-05 | 23.7681 | 224.7032 | 2007-12-05 | 23.1879 | 223.5069
2004-12-06 | 23.0434 | 224.3724 | 2005-12-06 | 22.8309 | 222.921 | 2006-12-06 | 23.7251 | 224.8044 | 2007-12-06 | 18.5866 | 225.4212
2004-12-07 | 22.9003 | 223.0026 | 2005-12-07 | 22.8309 | 222.921 | 2006-12-07 | 24.0384 | 225.368 | 2007-12-07 | 12.2218 | 195.1135
2004-12-08 | 22.7871 | 222.5937 | 2005-12-08 | 22.2274 | 221.3443 | 2006-12-08 | 23.7067 | 224.0873 | 2007-12-08 | 20.0326 | 215.2438
2004-12-09 | 22.7968 | 222.7023 | 2005-12-09 | 22.6157 | 222.2913 | 2006-12-09 | 23.8455 | 225.1305 | 2007-12-09 | 24.0009 | 225.6157
2004-12-10 | 22.2632 | 221.2725 | 2005-12-10 | 22.8959 | 222.7872 | 2006-12-10 | 23.7261 | 224.865 | 2007-12-10
2004-12-11 | 23.1771 | 223.5179 | 2005-12-11 | 22.8673 | 224.0634 | 2006-12-11 | 23.5094 | 224.9476 | 2007-12-11 | 23.8846 | 225.3522
2004-12-12 | 22.4687 | 222.2206 | 2005-12-12 | 22.0912 | 221.1149 | 2006-12-12 |  |  | 2007-12-12 | 23.9087 | 225.2352
2004-12-13 | 22.6715 | 222.4429 | 2005-12-13 | 23.5876 | 224.4136 | 2006-12-13 | 22.9948 | 224.0166 | 2007-12-13 | 23.7076 | 224.9565
2004-12-14 | 22.7594 | 222.6443 | 2005-12-14 | 22.0045 | 220.7296 | 2006-12-14 | 23.3002 | 223.8236 | 2007-12-14 | 23.6279 | 224.823
2004-12-15 | 21.7672 | 219.7851 | 2005-12-15 | 0 | 0 | 2006-12-15 | 23.5007 | 224.2068 | 2007-12-15 | 23.8409 | 225.3454
2004-12-16 | 22.4312 | 221.9874 | 2005-12-16 | 14.3811 | 198.4192 | 2006-12-16 | 23.7715 | 224.8937 | 2007-12-16 | 23.8086 | 225.1803
2004-12-17 | 23.0042 | 223.2066 | 2005-12-17 | 23.155 | 223.5573 | 2006-12-17 | 22.2924 | 221.3354 | 2007-12-17 | 23.9157 | 225.5264
2004-12-18 | 23.0042 | 223.2066 | 2005-12-18 | 23.155 | 223.5573 | 2006-12-18 | 16.494 | 206.4069 | 2007-12-18 | 24.0922 | 225.5987
2004-12-19 | 22.8621 | 223.0802 | 2005-12-19 | 23.1009 | 223.7651 | 2006-12-19 | 21.5979 | 219.2986 | 2007-12-19 | 23.9891 | 225.5694
2004-12-20 | 22.8508 | 222.7374 | 2005-12-20 |  |  | 2006-12-20 | 23.9929 | 225.3614 | 2007-12-20 | 23.8034 | 225.1376
2004-12-21 | 22.5811 | 222.1057 | 2005-12-21 | 0 | 0 | 2006-12-21 | 23.7476 | 224.9196 | 2007-12-21 | 23.7571 | 225.0544
2004-12-22 | 23.28 | 223.9149 | 2005-12-22 | 23.5836 | 224.5996 | 2006-12-22 | 24.1487 | 225.5422 | 2007-12-22 | 23.8666 | 225.3154
2004-12-23 | 23.4713 | 224.3869 | 2005-12-23 | 23.8012 | 225.0275 | 2006-12-23 | 23.4731 | 224.3385 | 2007-12-23 | 24.722 | 227.2278
2004-12-24 | 23.1733 | 224.456 | 2005-12-24 | 22.9632 | 223.229 | 2006-12-24 | 23.8631 | 225.0397 | 2007-12-24 | 23.5257 | 224.999
2004-12-25 | 23.2453 | 222.9958 | 2005-12-25 | 22.9815 | 223.2603 | 2006-12-25 | 24.1784 | 225.0791 | 2007-12-25 | 23.8335 | 225.3337
2004-12-26 |  |  | 2005-12-26 |  |  | 2006-12-26 | 23.6266 | 224.2631 | 2007-12-26 | 23.834 | 224.6129
2004-12-27 | 22.9516 | 222.4691 | 2005-12-27 | 0 | 0 | 2006-12-27 | 23.8497 | 225.4128 | 2007-12-27 | 23.9042 | 225.4435
2004-12-28 | 23.0809 | 223.3669 | 2005-12-28 | 22.7939 | 222.8882 | 2006-12-28 |  |  | 2007-12-28 | 23.971 | 225.4837
2004-12-29 | 22.779 | 223.0502 | 2005-12-29 | 22.7691 | 222.8406 | 2006-12-29 | 23.9384 | 225.454 | 2007-12-29 | 23.6706 | 224.9499
2004-12-30 | 22.6357 | 222.6463 | 2005-12-30 | 21.5747 | 217.5154 | 2006-12-30 | 24.229 | 225.9539 | 2007-12-30 | 24.0916 | 225.5437
2004-12-31 | 23.1503 | 223.587 | 2005-12-31 | 23.1215 | 223.6864 | 2006-12-31 | 23.8552 | 225.0579 | 2007-12-31 | 23.7607 | 224.9118

## Electricity Demand
ELECTRICAL POWER USAGE FIGURE
I. | MAIN EQUIPMENT
|  |  | Before project |  | After project
No. | Equipment | Description | 132 TPD rate | 147 TPD with New Blower | 147 TPD with Power Gen
|  |  | kW | kW | kW
1 | P-108 | Sulfur Unloading Pump | 10.5998 | 10.5998 | 10.5998
2 | P-263/264 | Hot Water Circulation Pump | 3.4294 | 3.4294 | 3.4294
4 | P-273/274 | Recycle Sulfur Pump | 10.101 | 10.101 | 10.101
6 | P-303/304 | Stabilizer Feed Pump | 2.307 | 2.307 | 2.307
8 | P-308 | Stripper Reflux Pump | 2.0576 | 2.0576 | 2.0576
9 | P-323/324 | Rich Oil Pump | 9.2281 | 9.2281 | 9.2281
11 | P-333 | Absorber Intercooler Pump | 3.0552 | 3.0552 | 3.0552
12 | P-353/354 | Lean Oil Pump | 12.2833 | 12.2833 | 12.2833
14 | P-433/434 | Still Reflux Pump | 6.2352 | 6.2352 | 6.2352
16 | P-501 | KO Drum Pump | 2.307 | 2.307 | 2.307
17 | P-541 | Steam Condenser fan | 4.7388 | 4.7388 | 4.7388
18 | P-573/574 | Recovered Sulfur Pump | 19.2044 | 19.2044 | 19.2044
20 | P-579 | Sulfur Basin Pump | 1.6461 | 1.6461 | 1.6461
21 | K-504 | Combustion Blower | 0 | 400 | 400
22 | P-603/604 | Pad Water Pump | 6.0481 | 6.0481 | 6.0481
24 | P-683 | CS2 Vent Scrubber Pump | 2.8682 | 2.8682 | 2.8682
25 | P-783 | Waste Water Stripper | 1.4341 | 1.4341 | 1.4341
26 | P-768 | Collector Tank Pump | 0 | 0 | 0
29 | P-810 | Utility Sump Pump | 1.247 | 1.247 | 1.247
30 | P-824/825 | Demin Transfer Pump | 2.7435 | 2.7435 | 2.7435
32 | P-826/827 | Desuperheater Pump | 1.247 | 1.247 | 1.247
34 | P-804 | Indion Pump | 3.18 | 3.18 | 3.18
35 | P-833/834 | Boiler Feed Water Pump | 42.7735 | 42.7735 | 42.7735
37 | P-842 | FD Fan Boiler | 4.9882 | 4.9882 | 4.9882
38 | P-894/895 | Air Cooler Condenser | 24.3173 | 24.3173 | 0
40 | P-903/904 | Cooling Water Pump | 221.3496 | 221.3496 | 221.3496
42 | P-905 | Cooling Tower Fan | 43.6464 | 43.6464 | 43.6464
43 | A-920/930 | Instrument Air Compressor | 62.2273 | 62.2273 | 62.2273
45 | P-973 | Process Water Pump | 4.8011 | 4.8011 | 4.8011
46 | P-974/975 | Safety Shower Pump | 2.3694 | 2.3694 | 2.3694
48 | P-981 | Waste Water Pump | 12.4704 | 12.4704 | 12.4704
49 | P-989 | Oil Skimmer | 0.31176 | 0.31176 | 0.31176
52 | MG1/2 | Motor Gate 1 | 0.62352 | 0.62352 | 0.62352
Sub Total I (kW) |  |  | 525.8394 | 925.8394 | 901.5221
II. | ADDITIONAL EQUIPMENT FOR TURBINE GENSET
1 | P-905/906 | Cooling Water pump (90KW) |  |  | 89.7869
2 | P-907 | Cooling tower fan (40KW) |  |  | 39.9053
3 | P-852 | Condensate pump(7.5KW) |  |  | 7.4822
4 | AOP | Auxiliary oil pump(5KW) |  |  | 0
Sub Total II (kW) |  |  |  |  | 137.1744
III. | OFFICE AND PANEL
1 | WTR.TRMT | Water Treatment | 3.367 | 3.367 | 3.367
2 | PKG-A-910 | Dosing Pump | 0.62352 | 0.62352 | 0.62352
3 | PKG-A-990 | Fire Water | 6.547 | 6.547 | 6.547
5 | LP-B-002 | Office Building Lighting Panel | 7.794 | 7.794 | 7.794
6 | LP-B-003 | Control Building Lighting Panel | 13.281 | 13.281 | 13.281
7 | LP-B-004 | Utility Building Lighting Panel | 7.6693 | 7.6693 | 7.6693
8 | 500-EL | SRU | 1.5588 | 1.5588 | 1.5588
9 | UPS001 | UPS for DCS | 6.6717 | 6.6717 | 6.6717
10 | UPS003 | UPS for Office , Furnace,etc. | 8.4175 | 8.4175 | 8.4175
11 | P-BDC-001 | 110 VDC Charger | 2.6811 | 2.6811 | 2.6811
13 | LP-A-002 | Shelter Lighting | 0 | 0 | 0
14 | PP-A-001 | Mechanic Workshop | 2.9929 | 2.9929 | 2.9929
15 | PP-A-002 | Electric Workshop | 2.9929 | 2.9929 | 2.9929
16 | PP-A-003 | AC Control Building | 22.5714 | 22.5714 | 22.5714
17 | PP-A-004 | AC Office Building | 14.5904 | 14.5904 | 14.5904
18 | PANJI | PANJI Office and Warehouse | 17.5209 | 17.5209 | 17.5209
19 | HVAC | Control Building HVAC | 13.0939 | 13.0939 | 13.0939
Sub Total III (kW) |  |  | 132.3733 | 132.3733 | 132.3733
Total (kW) |  |  | 658.2127 | 1058.2127 | 1171.0698